## 167_6
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal Style | [9 empty] | Universal Style | [9 empty] | Universal Style | [9 empty] | Universal Style
"N" Speed (TCC 167-6) | [9 empty] | "N" Speed (TCC 167-6) | [9 empty] | "N" Speed (TCC 167-6) | [9 empty] | "N" Speed (TCC 167-6)
Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated January 20, 1986
Tolerance in Terms of Current: Plus 10% for links rated 10N thru 100N; Plus 20% for links rated 125N thru 200N | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10N thru 100N; Plus 20% for links rated 125N thru 200N | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10N thru 100N; Plus 20% for links rated 125N thru 200N | [9 empty] | Tolerance in Terms of Current: Plus 10% for links rated 10N thru 100N; Plus 20% for links rated 125N thru 200N
5N |  | 8N |  | 10N |  | 15N |  | 20N |  | 25N |  | 30N |  | 40N |  | 45N |  | 50N |  | 65N |  | 75N |  | 85N |  | 95N |  | 100N |  | 125N |  | 150N |  | 200N
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
181.153 | 0.01 | 229.142 | 0.01 | 281.559 | 0.01 | 334.736 | 0.01 | 446.011 | 0.01 | 544.759 | 0.01 | 698.086 | 0.01 | 766.89 | 0.01 | 1208.75 | 0.01 | 1422.74 | 0.01 | 1788.87 | 0.01 | 2167.52 | 0.01 | 2934.64 | 0.01 | 3910.19 | 0.01 | 4756.85 | 0.01 | 6041.09 | 0.01 | 7921.53 | 0.01 | 10000 | 0.017472
169.923 | 0.011354 | 213.011 | 0.011491 | 263.05 | 0.011491 | 313.357 | 0.011366 | 416.274 | 0.011457 | 510.476 | 0.011411 | 651.543 | 0.011445 | 715.043 | 0.011526 | 1144.06 | 0.01123 | 1334.54 | 0.011377 | 1676.29 | 0.011423 | 2027.06 | 0.0114 | 2741.72 | 0.011468 | 3642.19 | 0.011457 | 4453.03 | 0.0114 | 5700.68 | 0.011286 | 7550.28 | 0.011063 | 9436.5 | 0.019542
151.463 | 0.01429 | 189.113 | 0.014579 | 237.542 | 0.01412 | 290.715 | 0.013218 | 381.589 | 0.013634 | 470.287 | 0.013431 | 600.849 | 0.013431 | 641.843 | 0.014376 | 1056.1 | 0.013165 | 1206.33 | 0.013951 | 1533.55 | 0.013662 | 1856.3 | 0.013634 | 2528.4 | 0.013512 | 3355.45 | 0.013445 | 3871.28 | 0.015098 | 5122.2 | 0.013979 | 6962.82 | 0.013008 | 8650.22 | 0.023025
136.093 | 0.017647 | 169.753 | 0.018022 | 213.865 | 0.017419 | 256.555 | 0.016972 | 342.182 | 0.016955 | 424.259 | 0.01652 | 535.041 | 0.016955 | 572.689 | 0.017986 | 974.908 | 0.015481 | 1099.2 | 0.016803 | 1417.06 | 0.015968 | 1657.95 | 0.017023 | 2292.37 | 0.016471 | 3082.02 | 0.01592 | 3516.92 | 0.018313 | 4565.76 | 0.017594 | 6453.26 | 0.015129 | 7977.18 | 0.02702
122.528 | 0.021837 | 151.312 | 0.02275 | 190.251 | 0.022078 | 225.28 | 0.021924 | 308.383 | 0.02073 | 382.735 | 0.020279 | 488.014 | 0.020279 | 520.268 | 0.021924 | 875.98 | 0.019155 | 1001.58 | 0.020198 | 1282.21 | 0.019503 | 1455.84 | 0.022167 | 2120.36 | 0.019329 | 2785.94 | 0.019406 | 3125.47 | 0.023141 | 4049.47 | 0.0223 | 5763.73 | 0.019003 | 7203.63 | 0.033135
110.315 | 0.026859 | 133.265 | 0.029329 | 171.974 | 0.026966 | 202.217 | 0.026993 | 273.511 | 0.02638 | 340.135 | 0.025754 | 445.12 | 0.024425 | 462.36 | 0.027621 | 797.389 | 0.023117 | 920.892 | 0.023941 | 1157.87 | 0.023845 | 1310.73 | 0.027346 | 1961.26 | 0.022614 | 2498.24 | 0.024037 | 2805.51 | 0.028835 | 3591.55 | 0.028236 | 5101.76 | 0.024303 | 6544.24 | 0.040149
98.2333 | 0.033974 | 115.971 | 0.038652 | 154.987 | 0.033234 | 185.183 | 0.032091 | 243.555 | 0.033135 | 309.001 | 0.031081 | 399.951 | 0.030313 | 413.784 | 0.034764 | 705.808 | 0.029565 | 839.111 | 0.028806 | 1025.91 | 0.030465 | 1161.35 | 0.034834 | 1787.08 | 0.027237 | 2267.29 | 0.029067 | 2513.27 | 0.035859 | 3285.72 | 0.033771 | 4444.13 | 0.031836 | 5856.69 | 0.049829
88.177 | 0.042123 | 103.063 | 0.048647 | 141.506 | 0.039988 | 164.078 | 0.041001 | 219.718 | 0.040674 | 274.608 | 0.039354 | 366.26 | 0.036111 | 367.728 | 0.04415 | 638.641 | 0.036328 | 739.773 | 0.037099 | 924.583 | 0.037472 | 1059.27 | 0.041871 | 1612.18 | 0.033268 | 1967.15 | 0.038344 | 2238 | 0.045358 | 2850.76 | 0.044638 | 3902.37 | 0.041206 | 5294.06 | 0.061044
78.598 | 0.053175 | 90.8624 | 0.062652 | 123.266 | 0.052699 | 147.871 | 0.050582 | 196.83 | 0.050632 | 244.287 | 0.04963 | 328.108 | 0.045087 | 330.083 | 0.055069 | 566.991 | 0.045952 | 660.068 | 0.046599 | 831.593 | 0.046274 | 966.173 | 0.050481 | 1452.93 | 0.041042 | 1765.77 | 0.047588 | 1895.69 | 0.063155 | 2448.77 | 0.060315 | 3443.83 | 0.053069 | 4625.5 | 0.079566
68.1933 | 0.070569 | 81.1538 | 0.07846 | 111.424 | 0.064302 | 133.265 | 0.062277 | 178.813 | 0.061288 | 216.23 | 0.063408 | 296.884 | 0.055014 | 295.404 | 0.068964 | 506.915 | 0.057604 | 600.248 | 0.05652 | 747.208 | 0.057202 | 871.611 | 0.061904 | 1309.42 | 0.050582 | 1575.52 | 0.059715 | 1684.69 | 0.080286 | 2126.73 | 0.080125 | 2999.92 | 0.070217 | 4168.62 | 0.098257
60.7852 | 0.088641 | 71.618 | 0.10105 | 98.6271 | 0.082236 | 119.264 | 0.077447 | 163.097 | 0.07367 | 192.933 | 0.079407 | 274.059 | 0.064624 | 268.095 | 0.084318 | 453.658 | 0.071923 | 550.234 | 0.067396 | 655.464 | 0.074113 | 779.259 | 0.077138 | 1159.03 | 0.064045 | 1414.23 | 0.073891 | 1527.43 | 0.097572 | 1897.59 | 0.099942 | 2615.84 | 0.092074 | 3779.47 | 0.12073
54.1819 | 0.11134 | 63.583 | 0.1282 | 89.5991 | 0.099444 | 106.202 | 0.097767 | 146.4 | 0.091158 | 168.4 | 0.10433 | 254.511 | 0.074783 | 244.531 | 0.10145 | 392.817 | 0.096312 | 509.456 | 0.078696 | 594.276 | 0.090522 | 702.99 | 0.095163 | 1032.09 | 0.080688 | 1249.3 | 0.094594 | 1401.56 | 0.11612 | 1756.96 | 0.11705 | 2378.77 | 0.11201 | 3454.18 | 0.14658
47.5768 | 0.14354 | 55.3317 | 0.17082 | 80.3463 | 0.12391 | 93.9108 | 0.12529 | 131.939 | 0.11246 | 150.106 | 0.13118 | 234.239 | 0.088463 | 217.314 | 0.12923 | 353.663 | 0.11918 | 468.878 | 0.092999 | 536.112 | 0.11145 | 640.56 | 0.11439 | 912.641 | 0.1034 | 1112.47 | 0.11918 | 1264.38 | 0.14296 | 1620.26 | 0.13916 | 2139.53 | 0.14098 | 3172.71 | 0.17567
42.0284 | 0.18284 | 48.9278 | 0.21911 | 72.049 | 0.15425 | 84.4657 | 0.15441 | 118.907 | 0.13805 | 135.415 | 0.16119 | 211.525 | 0.10848 | 193.513 | 0.16412 | 316.506 | 0.1482 | 433.262 | 0.10892 | 486.552 | 0.13558 | 570.974 | 0.14469 | 821.673 | 0.1282 | 994.602 | 0.1491 | 1168.34 | 0.16743 | 1530.48 | 0.15658 | 1947.57 | 0.17253 | 2828.04 | 0.22851
36.6109 | 0.23951 | 44.5381 | 0.26549 | 62.324 | 0.20533 | 75.8946 | 0.19279 | 108.023 | 0.1666 | 120.342 | 0.20471 | 194.094 | 0.12846 | 173.876 | 0.20369 | 284.389 | 0.18412 | 393.603 | 0.13237 | 440.25 | 0.16577 | 514.576 | 0.17832 | 744.969 | 0.15565 | 903.56 | 0.18156 | 1059.27 | 0.20267 | 1422.74 | 0.18412 | 1744.7 | 0.21911 | 2655.37 | 0.26496
31.9875 | 0.31438 | 40.0587 | 0.33116 | 55.2211 | 0.26233 | 69.7101 | 0.22851 | 98.2333 | 0.20267 | 106.202 | 0.26259 | 179.351 | 0.15074 | 157.015 | 0.2528 | 259.393 | 0.2211 | 365.163 | 0.15394 | 390.467 | 0.21031 | 473.117 | 0.21349 | 674.076 | 0.1903 | 837.434 | 0.21243 | 975.883 | 0.23999 | 1333.2 | 0.21137 | 1567.66 | 0.27688 | 2495.74 | 0.30723
28.3988 | 0.40165 | 36.4648 | 0.40085 | 49.8165 | 0.32298 | 63.8378 | 0.27358 | 89.0632 | 0.24779 | 93.9108 | 0.34193 | 166.391 | 0.17462 | 145.088 | 0.29964 | 243.555 | 0.25078 | 342.524 | 0.17602 | 355.08 | 0.25662 | 431.964 | 0.25842 | 611.15 | 0.2315 | 774.597 | 0.24978 | 877.733 | 0.29964 | 1239.35 | 0.24804 | 1401.56 | 0.35517 | 2345.7 | 0.35731
25.466 | 0.50502 | 33.6949 | 0.47229 | 46.4486 | 0.37375 | 57.0738 | 0.34605 | 81.1538 | 0.30296 | 86.9511 | 0.40448 | 155.142 | 0.20045 | 132.733 | 0.3638 | 229.371 | 0.28418 | 313.984 | 0.21116 | 324.194 | 0.30815 | 393.21 | 0.31564 | 557.991 | 0.27744 | 705.102 | 0.30631 | 791.036 | 0.37375 | 1156.71 | 0.28934 | 1279.65 | 0.43685 | 2222.39 | 0.41182
23.0196 | 0.62553 | 30.8565 | 0.57226 | 44.316 | 0.41265 | 52.9499 | 0.40813 | 75.0644 | 0.3591 | 79.3085 | 0.49899 | 144.798 | 0.23197 | 125.004 | 0.41763 | 216.23 | 0.32073 | 279.595 | 0.26951 | 297.182 | 0.37077 | 364.798 | 0.37226 | 520.788 | 0.31977 | 638.641 | 0.3813 | 744.969 | 0.42436 | 1066.71 | 0.34675 | 1137.22 | 0.57628 | 2105.57 | 0.47466
21.0383 | 0.76097 | 28.3137 | 0.69131 | 41.7352 | 0.47041 | 49.8663 | 0.46572 | 70.7637 | 0.41018 | 74.2432 | 0.5844 | 135.55 | 0.26656 | 118.432 | 0.47276 | 204.659 | 0.36018 | 254.511 | 0.3295 | 274.333 | 0.44168 | 337.088 | 0.4439 | 487.038 | 0.36708 | 586.014 | 0.46201 | 706.514 | 0.47656 | 998.588 | 0.40165 | 1061.39 | 0.68239 | 1998.88 | 0.54927
18.9982 | 0.94823 | 25.466 | 0.87358 | 39.5018 | 0.53251 | 46.4951 | 0.5449 | 66.6427 | 0.47182 | 70.5517 | 0.66354 | 127.401 | 0.30539 | 111.982 | 0.54326 | 193.706 | 0.4061 | 232.373 | 0.40206 | 252.988 | 0.52985 | 315.243 | 0.51574 | 453.204 | 0.42777 | 541.5 | 0.55479 | 660.068 | 0.55424 | 937.618 | 0.46387 | 1014.69 | 0.76402 | 1893.8 | 0.63498
17.9456 | 1.0734 | 23.626 | 1.0354 | 37.4627 | 0.6022 | 43.5255 | 0.63562 | 62.7618 | 0.54599 | 67.5823 | 0.73848 | 119.384 | 0.35128 | 107.055 | 0.60886 | 181.334 | 0.46947 | 214.722 | 0.47751 | 237.542 | 0.61191 | 292.464 | 0.61253 | 420.878 | 0.49949 | 498.37 | 0.6783 | 623.496 | 0.63245 | 887.442 | 0.52668 | 971.016 | 0.85628 | 1801.44 | 0.73186
16.7324 | 1.2546 | 21.875 | 1.2446 | 35.4225 | 0.68581 | 41.1139 | 0.72967 | 59.0477 | 0.63308 | 64.7378 | 0.83264 | 112.656 | 0.40326 | 101.936 | 0.69408 | 170.604 | 0.53571 | 199.605 | 0.56543 | 223.708 | 0.70317 | 277.09 | 0.69617 | 391.64 | 0.58324 | 462.822 | 0.81289 | 586.014 | 0.73186 | 834.091 | 0.61008 | 930.147 | 0.95298 | 1718.73 | 0.84437
15.695 | 1.4533 | 20.663 | 1.4374 | 33.4598 | 0.7865 | 38.9526 | 0.83848 | 56.2241 | 0.71666 | 61.5805 | 0.94918 | 106.521 | 0.45925 | 96.5775 | 0.80803 | 161.474 | 0.60886 | 189.681 | 0.63689 | 210.049 | 0.81696 | 263.84 | 0.78415 | 361.891 | 0.69408 | 431.964 | 0.96449 | 553.545 | 0.841 | 794.206 | 0.68375 | 897.257 | 1.0521 | 1638.18 | 0.97515
14.8849 | 1.6518 | 19.616 | 1.6353 | 32.0195 | 0.87883 | 36.8681 | 0.96352 | 53.482 | 0.8227 | 58.5187 | 1.0973 | 100.518 | 0.53091 | 92.3278 | 0.9147 | 152.985 | 0.69339 | 179.889 | 0.72458 | 196.83 | 0.96064 | 251.475 | 0.88059 | 340.816 | 0.79441 | 407.216 | 1.1228 | 526.548 | 0.95298 | 759.259 | 0.76249 | 865.531 | 1.1547 | 1567.66 | 1.1239
14.1873 | 1.8457 | 18.622 | 1.8792 | 30.4884 | 0.99585 | 35.0349 | 1.1061 | 50.8737 | 0.95108 | 55.4979 | 1.2877 | 96.7708 | 0.58733 | 88.0888 | 1.049 | 144.798 | 0.79361 | 171.63 | 0.81942 | 186.297 | 1.1172 | 238.494 | 1.0099 | 323.223 | 0.89748 | 384.269 | 1.3163 | 501.871 | 1.0756 | 713.615 | 0.88589 | 834.926 | 1.2812 | 1500.18 | 1.2928
13.6446 | 2.0276 | 17.8561 | 2.1188 | 28.7992 | 1.1605 | 33.4933 | 1.2521 | 48.7325 | 1.0799 | 53.0029 | 1.4916 | 92.9764 | 0.64911 | 84.974 | 1.1686 | 139.26 | 0.87533 | 162.445 | 0.94161 | 176.68 | 1.2851 | 228.684 | 1.1307 | 304.096 | 1.0334 | 363.705 | 1.5416 | 481.71 | 1.2054 | 678.811 | 1.0028 | 802.188 | 1.4403 | 1434.17 | 1.4991
13.2149 | 2.2097 | 17.2247 | 2.351 | 27.3672 | 1.3362 | 31.8917 | 1.4403 | 46.6814 | 1.2298 | 51.2311 | 1.6902 | 89.2415 | 0.72458 | 82.0514 | 1.3124 | 133.132 | 0.98495 | 154.987 | 1.0659 | 169.075 | 1.4548 | 217.097 | 1.2954 | 287.535 | 1.191 | 342.867 | 1.8346 | 463.285 | 1.3349 | 645.06 | 1.1432 | 768.425 | 1.6419 | 1373.8 | 1.7278
12.7987 | 2.4057 | 16.7659 | 2.5724 | 25.8509 | 1.5665 | 30.5189 | 1.6402 | 44.9858 | 1.3866 | 49.469 | 1.9403 | 85.0591 | 0.82931 | 79.8656 | 1.4606 | 126.766 | 1.1217 | 148.761 | 1.1982 | 162.283 | 1.6419 | 207.544 | 1.4694 | 271.875 | 1.37 | 327.78 | 2.1103 | 444.675 | 1.5006 | 612.374 | 1.3124 | 736.083 | 1.8698 | 1315.98 | 2.0074
12.4205 | 2.6244 | 16.2704 | 2.8373 | 24.7134 | 1.7822 | 29.2052 | 1.8829 | 43.482 | 1.5634 | 48.3442 | 2.1921 | 81.3976 | 0.93973 | 77.5053 | 1.6567 | 121.309 | 1.2723 | 142.5 | 1.3442 | 156.232 | 1.8291 | 196.634 | 1.7123 | 255.786 | 1.6158 | 314.613 | 2.4202 | 426.812 | 1.6851 | 583.674 | 1.4916 | 708.637 | 2.1167 | 1266.91 | 2.3091
12.0654 | 2.8744 | 15.8528 | 3.1577 | 23.7444 | 2.0255 | 28.0881 | 2.1508 | 42.2391 | 1.7645 | 47.0093 | 2.557 | 77.8159 | 1.0777 | 75.3652 | 1.8811 | 116.203 | 1.4331 | 135.957 | 1.5447 | 151.009 | 2.0439 | 188.169 | 1.9716 | 243.312 | 1.8568 | 304.4 | 2.707 | 411.308 | 1.8829 | 557.991 | 1.6902 | 688.381 | 2.3323 | 1220.89 | 2.6454
11.7558 | 3.1451 | 15.3843 | 3.5532 | 22.6769 | 2.3323 | 27.2307 | 2.4057 | 41.1139 | 1.9934 | 45.8945 | 3.0308 | 74.6153 | 1.2347 | 74.0948 | 2.104 | 112.544 | 1.5886 | 130.757 | 1.7382 | 146.546 | 2.2543 | 180.61 | 2.2633 | 234.239 | 2.0727 | 293.343 | 3.0952 | 398.355 | 2.0852 | 543.127 | 1.8218 | 664.705 | 2.6454 | 1175.37 | 3.0736
11.4541 | 3.5178 | 15.0194 | 3.9783 | 21.7659 | 2.664 | 26.2416 | 2.7617 | 40.0187 | 2.2792 | 44.7614 | 3.6724 | 71.6896 | 1.4317 | 72.6277 | 2.3746 | 109.108 | 1.7627 | 125.505 | 1.9834 | 142.073 | 2.4889 | 172.663 | 2.6349 | 224.605 | 2.344 | 282.123 | 3.625 | 384.269 | 2.3557 | 526.548 | 1.9894 | 647.645 | 2.9413 | 1137.22 | 3.5354
11.0601 | 4.0994 | 14.634 | 4.4944 | 20.9753 | 3.0308 | 25.5426 | 3.1045 | 39.0697 | 2.6035 | 43.8312 | 4.3791 | 69.4319 | 1.6386 | 71.4749 | 2.6322 | 106.096 | 1.95 | 121.674 | 2.2207 | 137.874 | 2.7589 | 166.391 | 3.0127 | 216.23 | 2.627 | 271.061 | 4.2539 | 373.285 | 2.627 | 509.966 | 2.1964 | 632.287 | 3.2833 | 1097 | 4.0871
10.7547 | 4.7867 | 14.3442 | 5.0827 | 20.2336 | 3.4482 | 24.7877 | 3.5817 | 38.2577 | 2.9798 | 42.9633 | 5.2743 | 67.6499 | 1.8661 | 70.1297 | 2.9947 | 103.58 | 2.1251 | 118.314 | 2.4617 | 133.933 | 3.0797 | 160.187 | 3.5178 | 208.376 | 2.9649 | 263.313 | 4.8251 | 359.367 | 3.046 | 497.374 | 2.3746 | 613.6 | 3.7466 | 1059.27 | 4.7154
10.4578 | 5.6285 | 14.0742 | 5.6964 | 19.6356 | 3.8607 | 24.2483 | 4.0953 | 37.5753 | 3.4036 | 42.1969 | 6.5328 | 65.8478 | 2.1551 | 69.0856 | 3.4002 | 101.326 | 2.3114 | 115.162 | 2.7452 | 129.586 | 3.5213 | 155.608 | 4.0465 | 201.008 | 3.3698 | 254.256 | 5.6173 | 349.095 | 3.4689 | 485.094 | 2.6035 | 598.45 | 4.2032 | 1026.94 | 5.4567
10.2918 | 6.2392 | 13.837 | 6.3907 | 19.0553 | 4.3835 | 23.6969 | 4.8445 | 36.9419 | 3.8995 | 41.4856 | 8.214 | 64.415 | 2.5114 | 67.6499 | 4.079 | 99.0224 | 2.5879 | 111.982 | 3.0952 | 126.008 | 3.9584 | 152.375 | 4.5852 | 194.483 | 3.7767 | 248.475 | 6.3779 | 337.763 | 4.0102 | 473.117 | 2.8859 | 580.763 | 4.903 | 996.593 | 6.2704
10.0678 | 7.2416 | 13.6174 | 7.1911 | 18.6593 | 4.9424 | 23.3441 | 5.6229 | 36.4648 | 4.3922 | 40.9088 | 10.2763 | 63.2659 | 2.8801 | 66.5761 | 4.7107 | 96.7708 | 2.9149 | 109.327 | 3.4689 | 123.266 | 4.4231 | 149.059 | 5.2848 | 188.358 | 4.2412 | 241.373 | 7.4696 | 328.108 | 4.6174 | 459.594 | 3.2344 | 566.424 | 5.6173 | 968.107 | 7.2706
9.9081 | 8.3968 | 13.428 | 8.1242 | 18.2351 | 5.6851 | 23.0196 | 6.8815 | 35.9219 | 5.1031 | 40.4613 | 12.464 | 62.2617 | 3.2866 | 65.5194 | 5.7193 | 94.8546 | 3.2997 | 106.734 | 3.9505 | 120.583 | 4.997 | 146.254 | 6.0608 | 184.259 | 4.6639 | 235.885 | 8.6525 | 318.73 | 5.322 | 446.457 | 3.6687 | 551.887 | 6.4938 | 945.149 | 8.3298
9.6731 | 10.6636 | 13.2679 | 8.9876 | 17.9456 | 6.3461 | 22.7223 | 8.2223 | 35.3517 | 6.0366 | 40.1389 | 14.8774 | 61.0899 | 3.9229 | 64.5439 | 6.6982 | 93.2557 | 3.7279 | 104.621 | 4.5442 | 118.551 | 5.5669 | 143.501 | 7.1053 | 179.71 | 5.2218 | 230.752 | 10.0627 | 311.482 | 6.0487 | 433.696 | 4.178 | 537.185 | 7.7434 | 920.892 | 9.6876
9.491 | 13.0507 | 13.1096 | 10.1537 | 17.5376 | 7.6511 | 22.4737 | 10.1132 | 34.9649 | 7.1053 | 39.8589 | 17.4413 | 60.0001 | 4.706 | 63.9017 | 7.7978 | 91.9593 | 4.1448 | 102.549 | 5.2796 | 116.436 | 6.3018 | 140.941 | 8.1894 | 176.151 | 5.7999 | 226.635 | 11.6679 | 302.579 | 7.2055 | 422.988 | 4.7249 | 523.922 | 9.16 | 899.054 | 11.1656
9.3031 | 16.5741 | 12.9662 | 11.414 | 17.1731 | 9.317 | 22.2056 | 12.8436 | 34.5824 | 8.5151 | 39.6205 | 21.3669 | 59.2251 | 5.5503 | 63.1395 | 9.1967 | 90.3188 | 4.7724 | 100.921 | 6.0245 | 114.359 | 7.4175 | 138.289 | 9.6104 | 172.491 | 6.5853 | 221.482 | 13.8577 | 295.109 | 8.4557 | 412.957 | 5.3647 | 513.035 | 10.7816 | 878.612 | 12.9597
9.1554 | 20.6733 | 12.8115 | 13.0246 | 16.9344 | 11.1545 | 22.0287 | 16.2622 | 34.3756 | 10.1132 | 39.3048 | 26.7049 | 58.6945 | 6.3843 | 62.5738 | 10.5893 | 88.8852 | 5.5781 | 99.2206 | 7.077 | 112.882 | 8.3716 | 136.502 | 11.2441 | 168.232 | 7.5371 | 218.622 | 16.1488 | 288.398 | 10.0026 | 402.358 | 6.1771 | 502.373 | 12.703 | 857.776 | 14.8774
9.0734 | 24.5287 | 12.6714 | 14.8774 | 16.7157 | 13.3945 | 21.8969 | 19.2179 | 34.0335 | 12.539 | 39.1479 | 33.1104 | 58.0524 | 7.4472 | 61.8274 | 12.6271 | 87.5619 | 6.3398 | 97.7434 | 8.3632 | 111.201 | 9.7556 | 134.201 | 13.4347 | 164.407 | 8.7132 | 216.014 | 18.3907 | 282.688 | 11.5865 | 395.181 | 6.8884 | 494.894 | 14.4811 | 838.272 | 17.3544
8.9741 | 29.425 | 12.5327 | 17.0277 | 16.5659 | 16.4915 | 21.7442 | 23.8038 | 33.7286 | 15.2846 | 39.1087 | 41.7144 | 57.4748 | 8.7744 | 61.151 | 15.1476 | 86.604 | 7.1839 | 95.7122 | 10.5049 | 109.875 | 11.5865 | 131.544 | 17.2333 | 161.474 | 9.9527 | 212.585 | 21.7116 | 277.09 | 13.5426 | 388.519 | 7.7512 | 486.552 | 16.6739 | 820.852 | 19.9822
8.8938 | 35.6535 | 12.408 | 19.6258 | 16.4011 | 20.3655 | 21.6574 | 29.8399 | 33.5268 | 18.7434 | 38.9137 | 52.3445 | 56.846 | 10.6636 | 60.482 | 18.7434 | 85.4 | 8.4473 | 94.193 | 12.8693 | 108.347 | 14.0812 | 129.327 | 21.4311 | 158.276 | 11.3912 | 210.049 | 24.8497 | 271.061 | 16.0201 | 379.306 | 9.0779 | 478.35 | 19.7439 | 802.991 | 23.0311
8.7965 | 43.3734 | 12.2478 | 22.8247 | 16.2866 | 25.5298 | 21.5709 | 36.8128 | 33.3263 | 23.8514 | 38.7971 | 68.2958 | 56.2804 | 12.7795 | 59.7606 | 23.7562 | 84.297 | 9.8537 | 93.0694 | 15.9242 | 107.055 | 16.8415 | 127.274 | 27.2716 | 155.453 | 13.2745 | 207.544 | 28.7847 | 265.959 | 18.6686 | 373.659 | 10.1944 | 472.172 | 23.0772 | 787.878 | 26.4127
8.7526 | 52.8178 | 12.138 | 26.2023 | 16.173 | 30.8719 | 21.5278 | 44.3382 | 33.0938 | 30.5953 | 38.7583 | 87.6936 | 55.7204 | 15.3152 | 59.1659 | 30.7486 | 83.2914 | 11.5749 | 92.1434 | 19.3529 | 105.884 | 20.0824 | 125.63 | 34.0846 | 153.138 | 15.4382 | 205.479 | 33.2431 | 261.476 | 22.128 | 368.464 | 11.5634 | 464.213 | 28.243 | 772.277 | 30.5647
8.6915 | 64.5764 | 11.9813 | 30.3212 | 16.1085 | 38.9332 | 21.4848 | 53.402 | 32.9947 | 39.4426 | 38.565 | 111.369 | 55.166 | 18.6313 | 58.6358 | 40.4816 | 82.5452 | 13.3277 | 91.5922 | 22.8247 | 104.83 | 24.1877 | 123.884 | 43.9849 | 150.557 | 18.5014 | 203.638 | 37.9719 | 257.326 | 25.7606 | 363.705 | 13.1161 | 457.302 | 34.5652 | 754.717 | 35.1578
8.6309 | 81.0324 | 11.8502 | 34.8777 | 16.0602 | 49.5929 | 21.4419 | 66.6762 | 32.863 | 49.5433 | 38.4111 | 140.449 | 54.7264 | 21.9298 | 58.1686 | 51.7719 | 81.6422 | 15.6872 | 90.5902 | 27.2989 | 103.995 | 27.8225 | 122.406 | 55.3042 | 148.464 | 21.6033 | 202.015 | 43.6345 | 252.988 | 30.9337 | 359.367 | 14.7736 | 451.847 | 40.3603 | 740.513 | 39.5216
8.5707 | 96.4331 | 11.7793 | 40.6438 | 16.0281 | 62.8561 | 21.3563 | 81.6016 | 32.7973 | 62.4801 | 38.2577 | 177.834 | 54.2361 | 26.1499 | 57.8207 | 66.4765 | 80.8298 | 18.8186 | 89.9583 | 32.8137 | 103.373 | 32.6827 | 120.946 | 72.0132 | 146.546 | 26.3336 | 200.005 | 51.3594 | 249.222 | 36.9974 | 354.371 | 16.8246 | 447.798 | 45.0083 | 728.759 | 43.5038
8.5194 | 118.255 | 11.6855 | 46.8451 | 16.0281 | 78.5589 | 21.2923 | 102.806 | 32.6664 | 85.5285 | 38.2195 | 222.705 | 53.8039 | 32.1961 | 57.5323 | 86.4745 | 80.1056 | 22.0617 | 88.9741 | 41.1345 | 102.652 | 39.3245 | 119.862 | 91.9136 | 144.798 | 31.3385 | 198.213 | 60.7549 | 246.249 | 43.8093 | 350.144 | 18.8562 | 442.9 | 50.1414 | 715.759 | 47.7437
8.4769 | 149.134 | 11.5923 | 54.2633 | 15.9801 | 99.868 | 21.2498 | 124.194 | 32.6337 | 111.257 | 38.2195 | 265.032 | 53.482 | 39.7594 | 57.1309 | 107.646 | 79.4673 | 25.7863 | 88.2652 | 52.8706 | 102.14 | 45.3245 | 119.145 | 116.611 | 143.645 | 36.8865 | 196.83 | 71.1542 | 242.825 | 52.4493 | 345.276 | 20.9229 | 435.87 | 56.4778 | 700.884 | 52.7122
8.4262 | 185.647 | 11.523 | 62.1685 | 15.9641 | 125.694 | 21.1861 | 154.138 | 32.6337 | 135.89 | 38.2195 | 299.122 | 53.2685 | 48.1754 | 56.6191 | 135.89 | 78.9919 | 30.5036 | 87.5619 | 64.5118 | 101.427 | 53.242 | 118.196 | 147.65 | 142.5 | 44.7391 | 194.677 | 88.3096 | 239.929 | 62.1685 | 339.456 | 23.8753 | 429.38 | 62.8561 | 687.693 | 57.5036
8.401 | 227.659 | 11.477 | 71.4393 | 15.9323 | 157.567 | 21.1861 | 193.998 | 32.6337 | 166.143 |  |  | 53.0559 | 58.1397 | 56.1679 | 170.349 | 78.4409 | 36.2285 | 87.0381 | 76.696 | 100.619 | 62.6678 | 117.02 | 186.578 | 141.648 | 52.8706 | 193.9 | 104.778 | 237.542 | 73.9101 | 334.736 | 27.4906 | 423.411 | 71.2253 | 670.714 | 64.1901
8.3842 | 263.447 | 11.4541 | 82.8349 | 15.9163 | 206.613 | 21.1226 | 235.768 | 32.6011 | 213.759 |  |  | 52.8441 | 71.8693 | 55.8878 | 222.26 | 77.9717 | 42.0916 | 86.5174 | 89.3757 | 100.217 | 75.2525 | 116.552 | 220.931 | 140.66 | 64.3186 | 192.163 | 125.568 | 234.943 | 87.7814 | 331.074 | 30.8102 | 412.132 | 84.3394 | 653.5 | 71.7974
8.334 | 303.642 | 11.3855 | 95.7604 | 15.8686 | 259.784 | 21.1015 | 275.297 | 32.536 | 255.15 |  |  | 52.4755 | 90.7265 | 55.7204 | 270.657 | 77.6604 | 51.2568 | 86.172 | 103.321 | 99.8177 | 90.8173 | 115.971 | 256.172 | 139.958 | 78.089 | 190.632 | 151.691 | 232.141 | 107.002 | 326.145 | 35.868 | 403.971 | 95.4736 | 638.003 | 80.3064
|  | 11.3514 | 110.261 | 15.8211 | 300.922 | 21.1015 | 303.339 | 32.6011 | 298.524 |  |  | 52.2138 | 115.914 | 55.7761 | 299.421 | 77.1187 | 61.7966 | 85.828 | 120.283 | 99.4192 | 109.711 | 115.624 | 300.621 | 139.399 | 91.1813 | 188.546 | 193.031 | 230.061 | 131.216 | 321.29 | 40.8476 | 394.786 | 109.273 | 619.767 | 92.9303
|  | 11.2948 | 126.703 | [8 empty] | 51.9533 | 145.017 |  |  | 76.8877 | 75.4786 | 85.4854 | 141.012 | 99.1214 | 128.618 |  |  | 138.704 | 109.273 | 187.044 | 231.563 | 227.771 | 161.555 | 317.14 | 46.2864 | 386.195 | 124.318 | 601.45 | 107.753
|  | 11.2385 | 146.328 | [8 empty] | 51.6942 | 181.971 |  |  | 76.6574 | 100.168 | 84.974 | 167.813 | 98.6271 | 160.75 |  |  | 138.289 | 129.263 | 185.925 | 269.307 | 225.731 | 197.719 | 312.106 | 52.9765 | 377.414 | 141.578 | 587.187 | 122.223
|  | 11.2273 | 168.991 | [8 empty] | 51.4879 | 222.483 |  |  | 76.275 | 124.567 | 84.6348 | 205.377 | 98.2333 | 192.645 |  |  | 137.874 | 153.676 | 185.183 | 298.524 | 223.932 | 236.004 | 305.926 | 62.1685 | 369.202 | 158.673 | 573.262 | 139.33
|  | 11.1824 | 196.537 | [8 empty] | 51.3336 | 262.92 |  |  | 76.0466 | 150.483 | 84.2127 | 244.9 | 97.8412 | 228.343 |  |  | 137.461 | 187.138 |  |  | 222.37 | 273.103 | 300.769 | 72.4465 | 360.807 | 177.124 | 563.599 | 155.376
|  | 11.1489 | 225.619 | [8 empty] | 51.2311 | 297.332 |  |  | 75.8946 | 178.546 | 84.0444 | 277.231 | 97.5481 | 264.238 |  |  | 137.187 | 221.152 |  |  | 222.148 | 299.122 | 295.109 | 83.5002 | 352.956 | 193.998 | 552.992 | 173.27
|  | 11.0933 | 261.609 | [12 empty] | 75.6673 | 217.859 | 84.0444 | 298.524 | 97.3532 | 299.122 |  |  | 136.913 | 261.871 |  |  |  |  | 289.554 | 97.9885 | 345.621 | 210.998 | 541.5 | 193.611
|  | 11.0601 | 300.021 | [12 empty] | 75.5161 | 257.456 | [6 empty] | 136.639 | 303.339 |  |  |  |  | 284.958 | 112.039 | 337.425 | 232.026 | 529.188 | 213.759
[16 empty] | 75.4406 | 301.223 | [12 empty] | 279.875 | 127.977 | 332.069 | 250.097 | 516.638 | 235.062
[30 empty] | 274.333 | 148.242 | 325.819 | 273.65 | 503.379 | 259.265
[30 empty] | 268.632 | 169.161 | 320.648 | 297.332 | 491.442 | 280.578
[30 empty] | 263.05 | 195.166 | 316.19 | 325.334 | 478.829 | 302.43
[30 empty] | 258.357 | 218.733 | 311.794 | 360.269 | 465.142 | 333.57
[30 empty] | 252.988 | 247.361 | 308.383 | 398.159 | 452.751 | 364.619
[30 empty] | 247.483 | 275.572 | 306.232 | 440.915 | 442.9 | 396.57
[30 empty] | 242.583 | 311.329 | 304.4 | 490.71 | 431.101 | 441.356
[30 empty] | 238.971 | 343.385 | 302.579 | 542.861 | 422.565 | 484.372
[30 empty] | 235.178 | 384.849 | 301.673 | 601.155 | 415.442 | 531.048
[30 empty] | 231.909 | 433.917 |  |  | 411.308 | 573.555
[30 empty] | 229.142 | 489.729 |  |  | 408.031 | 602.359
[30 empty] | 227.089 | 551.065
[30 empty] | 225.731 | 601.757