## 176_2
S&C Power Fuses - Type SMU-20 | [9 empty] | S&C Power Fuses - Type SMU-20
Very Slow Speed (TCC 176-2) | [9 empty] | Very Slow Speed (TCC 176-2)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
3947.86 | 0.01 | 4870.38 | 0.01 | 6197.67 | 0.01 | 8492.41 | 0.01 | 10667.1 | 0.01 | 13506.5 | 0.01 | 15427.8 | 0.01 | 16931.4 | 0.01
3865.82 | 0.010429 | 4750.13 | 0.010597 | 6056.75 | 0.01046 | 8183.93 | 0.0108 | 10300.3 | 0.010768 | 13173 | 0.010608 | 14986.8 | 0.010608 | 16381.8 | 0.010682
3762.84 | 0.011008 | 4554.76 | 0.011503 | 5836.74 | 0.01132 | 7722.77 | 0.012153 | 9632.79 | 0.012312 | 12443.1 | 0.011877 | 14114 | 0.011948 | 15320.2 | 0.012202
3622.53 | 0.011829 | 4289.51 | 0.012956 | 5540.99 | 0.012561 | 7179.09 | 0.014021 | 8847.83 | 0.014608 | 11567.1 | 0.013744 | 13225.8 | 0.013621 | 14313 | 0.013951
3418.4 | 0.013311 | 4039.71 | 0.014681 | 5207.88 | 0.014177 | 6587.49 | 0.016686 | 8192.12 | 0.017057 | 10688.5 | 0.016145 | 12148.1 | 0.016145 | 13199.4 | 0.01652
3200.07 | 0.015159 | 3744.07 | 0.01704 | 4865.52 | 0.016274 | 6099.29 | 0.019503 | 7524.56 | 0.020259 | 9817.56 | 0.019117 | 11069.2 | 0.019484 | 12099.6 | 0.01968
2998.68 | 0.017298 | 3483.97 | 0.01966 | 4491.44 | 0.019117 | 5529.92 | 0.023703 | 6980.86 | 0.023537 | 8909.99 | 0.023187 | 10228.4 | 0.022842 | 11158.1 | 0.023117
2804.35 | 0.019818 | 3184.11 | 0.023537 | 4129.57 | 0.022569 | 5069.15 | 0.028264 | 6373.65 | 0.028349 | 8005.85 | 0.028777 | 9366.81 | 0.02721 | 10167.2 | 0.027815
2591.33 | 0.023141 | 2901.34 | 0.028377 | 3835.01 | 0.026169 | 4609.75 | 0.034212 | 5772.89 | 0.034625 | 7179.09 | 0.035644 | 8698.69 | 0.031582 | 9292.17 | 0.033334
2408.91 | 0.026725 | 2643.68 | 0.03411 | 3540.16 | 0.030587 | 4251.08 | 0.04039 | 5223.53 | 0.042165 | 6521.95 | 0.043146 | 7894.55 | 0.03842 | 8475.44 | 0.040189
2237.08 | 0.031019 | 2396.89 | 0.041496 | 3334 | 0.034487 | 3804.46 | 0.050329 | 4731.17 | 0.051603 | 5652.92 | 0.057202 | 7121.89 | 0.047162 | 7722.77 | 0.048259
2092.11 | 0.035431 | 2197.18 | 0.049382 | 3146.13 | 0.038884 | 3508.45 | 0.058944 | 4229.88 | 0.064431 | 5064.08 | 0.071635 | 6191.47 | 0.062152 | 7107.66 | 0.057088
1939 | 0.041165 | 1974.22 | 0.06135 | 2881.1 | 0.046228 | 3254.94 | 0.068415 | 3647.98 | 0.086799 | 4509.44 | 0.08989 | 5513.35 | 0.078225 | 6450.6 | 0.06931
1809.72 | 0.047304 | 1822.43 | 0.072067 | 2599.12 | 0.056633 | 3007.69 | 0.080286 | 3200.07 | 0.11291 | 4104.87 | 0.10859 | 4909.5 | 0.098061 | 5948.7 | 0.081255
1642.42 | 0.057317 | 1660.59 | 0.086452 | 2351.78 | 0.069379 | 2726.92 | 0.09767 | 2881.1 | 0.13999 | 3759.08 | 0.12949 | 4415.73 | 0.12122 | 5415 | 0.097767
1492.08 | 0.069518 | 1545.23 | 0.099742 | 2100.49 | 0.086452 | 2532.41 | 0.11382 | 2545.11 | 0.17958 | 3367.51 | 0.16103 | 3987.53 | 0.1482 | 5043.87 | 0.11257
1337.99 | 0.086107 | 1447.98 | 0.11314 | 1893.02 | 0.10676 | 2305.21 | 0.13846 | 2266.35 | 0.2276 | 3050.1 | 0.1959 | 3582.9 | 0.1843 | 4568.45 | 0.13695
1213.09 | 0.10496 | 1335.32 | 0.1333 | 1724.91 | 0.12859 | 2100.49 | 0.1666 | 2058.9 | 0.27661 | 2838.21 | 0.22669 | 3184.11 | 0.23173 | 4146.12 | 0.1671
1113.12 | 0.12404 | 1235.12 | 0.1558 | 1563.88 | 0.1558 | 1910.13 | 0.20267 | 1844.43 | 0.34848 | 2586.16 | 0.27249 | 2826.88 | 0.29342 | 3740.33 | 0.20491
1036.83 | 0.14339 | 1128.82 | 0.18634 | 1440.76 | 0.18357 | 1761.51 | 0.23975 | 1667.24 | 0.42735 | 2389.71 | 0.31977 | 2519.78 | 0.36893 | 3364.14 | 0.25381
954.255 | 0.16878 | 1055.67 | 0.2137 | 1316.76 | 0.21955 | 1616.35 | 0.28646 | 1496.56 | 0.53732 | 2179.67 | 0.38207 | 2134.37 | 0.51677 | 2986.71 | 0.32105
871.252 | 0.20206 | 981.352 | 0.24656 | 1205.83 | 0.2618 | 1481.67 | 0.34227 | 1347.39 | 0.6729 | 1968.3 | 0.46759 | 1929.33 | 0.63435 | 2697.09 | 0.39449
790.71 | 0.24533 | 902.285 | 0.29166 | 1085.64 | 0.32298 | 1356.86 | 0.40895 | 1219.17 | 0.8318 | 1788.13 | 0.5677 | 1779.22 | 0.75189 | 2447.76 | 0.47895
736.516 | 0.28248 | 829.589 | 0.34536 | 1003.18 | 0.3794 | 1220.39 | 0.50907 | 1088.9 | 1.0638 | 1621.21 | 0.69966 | 1645.71 | 0.88589 | 2217.04 | 0.58969
673.798 | 0.33717 | 754.406 | 0.41888 | 918.674 | 0.45196 | 1112.01 | 0.61621 | 977.434 | 1.3496 | 1469.87 | 0.85286 | 1542.14 | 1.0109 | 2032.31 | 0.70598
612.122 | 0.40773 | 697.799 | 0.48911 | 838.765 | 0.54109 | 989.234 | 0.77557 | 872.996 | 1.7382 | 1297.15 | 1.1105 | 1415.06 | 1.2286 | 1883.58 | 0.83014
563.367 | 0.47991 | 636.466 | 0.5891 | 784.409 | 0.62116 | 901.384 | 0.94067 | 782.06 | 2.2431 | 1174.89 | 1.3741 | 1318.07 | 1.4317 | 1747.48 | 0.97418
523.706 | 0.55479 | 569.029 | 0.73553 | 731.378 | 0.71881 | 822.157 | 1.1375 | 697.101 | 2.9442 | 1084.56 | 1.6419 | 1237.6 | 1.637 | 1606.68 | 1.1675
480.07 | 0.65957 | 508.228 | 0.92852 | 680.57 | 0.83597 | 738.729 | 1.4317 | 632.026 | 3.7503 | 1003.18 | 1.9442 | 1183.14 | 1.8037 | 1452.33 | 1.4635
448.062 | 0.75718 | 464.022 | 1.1183 | 634.559 | 0.96835 | 675.823 | 1.7347 | 584.602 | 4.5715 | 933.491 | 2.2907 | 1112.01 | 2.0747 | 1347.39 | 1.7295
416.935 | 0.8762 | 426.21 | 1.3362 | 589.297 | 1.1296 | 617.038 | 2.1251 | 548.36 | 5.4241 | 873.869 | 2.6614 | 1048.3 | 2.3889 | 1256.3 | 2.0377
382.195 | 1.05 | 388.359 | 1.6337 | 551.108 | 1.3006 | 574.748 | 2.4889 | 510.776 | 6.6449 | 813.162 | 3.1419 | 988.245 | 2.7534 | 1178.42 | 2.3699
349.649 | 1.2596 | 357.785 | 1.9481 | 517.459 | 1.4946 | 530.029 | 2.9827 | 477.198 | 8.1323 | 766.574 | 3.6504 | 921.434 | 3.2898 | 1115.35 | 2.7097
318.28 | 1.5324 | 329.287 | 2.3346 | 486.351 | 1.7123 | 493.208 | 3.5319 | 450.758 | 9.7167 | 721.932 | 4.2539 | 872.996 | 3.7918 | 1053.56 | 3.1357
294.398 | 1.8146 | 302.152 | 2.8373 | 455.744 | 1.9815 | 462.632 | 4.1241 | 428.346 | 11.7147 | 673.125 | 5.1133 | 822.979 | 4.4765 | 992.206 | 3.7019
278.364 | 2.0459 | 278.643 | 3.431 | 424.508 | 2.3323 | 432.218 | 4.8785 | 409.498 | 14.0672 | 637.74 | 5.9885 | 777.381 | 5.2637 | 937.232 | 4.3355
257.735 | 2.4057 | 258.768 | 4.0953 | 402.595 | 2.6322 | 402.998 | 5.8524 | 394.229 | 16.8583 | 607.852 | 6.8747 | 730.647 | 6.3398 | 887.076 | 5.1133
236.969 | 2.9033 | 244.92 | 4.6966 | 381.05 | 3.0067 | 378.771 | 6.9577 | 378.014 | 20.902 | 578.207 | 8.0112 | 683.298 | 7.9157 | 835.417 | 6.0608
218.313 | 3.5003 | 232.509 | 5.3647 | 362.104 | 3.407 | 352.458 | 8.4811 | 363.192 | 25.9156 | 553.317 | 9.2243 | 649.973 | 9.3357 | 791.501 | 7.2416
202.539 | 4.1655 | 222.056 | 6.1524 | 344.788 | 3.8491 | 333.93 | 9.9826 | 351.754 | 31.8758 | 533.752 | 10.6105 | 618.892 | 10.9555 | 752.146 | 8.8008
189.603 | 4.9374 | 210.804 | 7.1911 | 330.607 | 4.2667 | 315.428 | 12.0353 | 340.676 | 40.5221 | 516.942 | 12.1441 | 595.816 | 12.7158 | 716.18 | 10.7816
177.493 | 5.829 | 201.327 | 8.3382 | 317.009 | 4.7676 | 298.847 | 14.4666 | 331.269 | 51.9794 | 501.163 | 13.8577 | 566.191 | 16.1326 | 688.098 | 12.9467
167.994 | 6.7723 | 193.046 | 9.6296 | 303.667 | 5.3701 | 286.555 | 17.0618 | 324.061 | 64.3186 | 487.325 | 15.8448 | 546.717 | 19.4694 | 657.162 | 15.7816
158.686 | 7.9315 | 184.921 | 11.1768 | 292.052 | 6.0065 | 275.595 | 19.9423 | 318.28 | 82.0927 | 470.564 | 18.8374 | 530.559 | 23.5199 | 630.133 | 19.3336
153.075 | 8.8008 | 177.848 | 12.9467 | 276.976 | 6.9646 | 262.941 | 25.2505 | 313.855 | 105.514 | 455.744 | 22.3504 | 513.85 | 29.016 | 608.46 | 23.3324
147.515 | 9.8143 | 171.731 | 14.9969 | 266.648 | 7.7667 | 252.127 | 31.4012 | 309.492 | 139.47 | 444.047 | 26.3863 | 496.176 | 37.2945 | 589.887 | 28.2995
142.869 | 10.9336 | 165.659 | 17.599 | 256.706 | 8.722 | 243.455 | 38.1622 | 306.412 | 175.361 | 431.786 | 31.5586 | 480.55 | 49.4938 | 570.168 | 35.0876
137.542 | 12.7412 | 159.961 | 20.7562 | 247.629 | 9.9031 | 236.26 | 46.5184 | 302.757 | 239.332 | 422.391 | 36.9234 | 467.749 | 65.1602 | 555.535 | 42.4721
133.344 | 14.612 | 155.078 | 24.5042 | 237.681 | 11.4369 | 228.59 | 58.6653 | 300.045 | 327.292 | 414.441 | 43.0278 | 457.113 | 86.2154 | 544.534 | 50.696
127.476 | 17.9008 | 151.552 | 28.3562 | 227.905 | 13.3143 | 221.613 | 76.0848 | 298.847 | 413.167 | 407.455 | 49.8914 | 448.51 | 110.813 | 536.427 | 59.3142
123.956 | 20.5497 | 147.663 | 34.3241 | 221.17 | 14.9819 | 215.278 | 99.968 | 297.952 | 524.189 | 399.387 | 60.5124 | 440.069 | 139.052 | 526.331 | 73.0284
119.933 | 24.4308 | 145.174 | 40.159 | 215.494 | 16.9428 | 210.594 | 128.618 | 297.654 | 598.157 | 392.262 | 73.1746 | 433.517 | 178.19 | 516.942 | 91.9136
116.621 | 28.8712 | 142.869 | 47.4107 | 208.916 | 19.5866 | 206.63 | 166.143 |  |  | 385.265 | 93.2095 | 427.49 | 227.887 | 509.246 | 113.732
113.855 | 34.0165 | 140.321 | 57.2741 | 203.35 | 22.5525 | 203.554 | 214.831 |  |  | 379.15 | 115.682 | 421.969 | 297.63 | 503.172 | 142.287
111.489 | 40.0387 | 138.232 | 69.1895 | 198.131 | 26.2023 | 200.323 | 283.965 |  |  | 374.253 | 142.145 | 419.444 | 382.547 | 498.165 | 178.368
109.501 | 46.9859 | 136.719 | 82.7521 | 193.82 | 30.2303 | 197.143 | 386.778 |  |  | 369.788 | 180.702 | 416.935 | 499.123 | 493.208 | 225.169
107.44 | 57.5036 | 135.088 | 104.151 | 189.792 | 34.9475 | 195.377 | 502.127 |  |  | 366.842 | 226.071 | 415.271 | 578.161 | 487.813 | 281.139
105.946 | 68.7756 | 133.344 | 130.692 | 185.848 | 40.8067 | 194.987 | 597.559 |  |  | 362.829 | 302.733 | 415.686 | 601.757 | 483.926 | 357.756
104.369 | 82.0107 | 131.753 | 181.971 | 182.168 | 47.6483 |  |  |  |  | 360.298 | 408.647 |  |  | 481.031 | 452.077
102.918 | 99.868 | 130.051 | 254.131 | 178.919 | 56.8177 |  |  |  |  | 358.86 | 542.861 |  |  | 480.07 | 552.721
101.792 | 126.703 | 129.015 | 339.289 | 175.903 | 67.8194 |  |  |  |  | 357.785 | 602.961 |  |  | 480.07 | 601.757
100.88 | 172.233 | 128.115 | 471.94 | 172.938 | 81.1135
100.377 | 220.269 | 127.604 | 584.556 | 169.853 | 99.968
99.7766 | 279.737 | 127.476 | 613.913 | 167.324 | 120.886
99.279 | 342.014 |  |  | 164.833 | 154.447
98.8826 | 445.346 |  |  | 162.866 | 188.642
98.6851 | 573.555 |  |  | 160.442 | 239.332
98.7838 | 609.631 |  |  | 159.004 | 290.281
|  |  |  | 156.95 | 391.448
|  |  |  | 155.856 | 540.153
|  |  |  | 155.544 | 598.755