## 692-9-C5
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Short-Time Inverse I.E.C. (C5) (TCC 692-9-C5) | [9 empty] | Short-Time Inverse I.E.C. (C5) (TCC 692-9-C5) | [9 empty] | Short-Time Inverse I.E.C. (C5) (TCC 692-9-C5)
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.05 |  | Time Dial = 0.1 |  | Time Dial = 0.2 |  | Time Dial = 0.3 |  | Time Dial = 0.4 |  | Time Dial = 0.5 |  | Time Dial = 0.6 |  | Time Dial = 0.7 |  | Time Dial = 0.8 |  | Time Dial = 0.9 |  | Time Dial = 1.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 0.1529 | 1.5 | 0.30579 | 1.5 | 0.61159 | 1.5 | 0.91738 | 1.5 | 1.2232 | 1.5 | 1.529 | 1.5 | 1.8348 | 1.5 | 2.1406 | 1.5 | 2.4464 | 1.5 | 2.7522 | 1.5 | 3.0579
1.6 | 0.13173 | 1.6 | 0.26346 | 1.6 | 0.52693 | 1.6 | 0.79039 | 1.6 | 1.0539 | 1.6 | 1.3173 | 1.6 | 1.5808 | 1.6 | 1.8442 | 1.6 | 2.1077 | 1.6 | 2.3712 | 1.6 | 2.6346
1.7 | 0.11654 | 1.7 | 0.23308 | 1.7 | 0.46616 | 1.7 | 0.69924 | 1.7 | 0.93231 | 1.7 | 1.1654 | 1.7 | 1.3985 | 1.7 | 1.6316 | 1.7 | 1.8646 | 1.7 | 2.0977 | 1.7 | 2.3308
1.8 | 0.10509 | 1.8 | 0.21017 | 1.8 | 0.42034 | 1.8 | 0.63052 | 1.8 | 0.84069 | 1.8 | 1.0509 | 1.8 | 1.261 | 1.8 | 1.4712 | 1.8 | 1.6814 | 1.8 | 1.8915 | 1.8 | 2.1017
1.9 | 0.09613 | 1.9 | 0.19226 | 1.9 | 0.38452 | 1.9 | 0.57678 | 1.9 | 0.76904 | 1.9 | 0.9613 | 1.9 | 1.1536 | 1.9 | 1.3458 | 1.9 | 1.5381 | 1.9 | 1.7303 | 1.9 | 1.9226
2 | 0.088924 | 2 | 0.17785 | 2 | 0.3557 | 2 | 0.53355 | 2 | 0.71139 | 2 | 0.88924 | 2 | 1.0671 | 2 | 1.2449 | 2 | 1.4228 | 2 | 1.6006 | 2 | 1.7785
2.1 | 0.082995 | 2.1 | 0.16599 | 2.1 | 0.33198 | 2.1 | 0.49797 | 2.1 | 0.66396 | 2.1 | 0.82995 | 2.1 | 0.99594 | 2.1 | 1.1619 | 2.1 | 1.3279 | 2.1 | 1.4939 | 2.1 | 1.6599
2.2 | 0.078025 | 2.2 | 0.15605 | 2.2 | 0.3121 | 2.2 | 0.46815 | 2.2 | 0.6242 | 2.2 | 0.78025 | 2.2 | 0.9363 | 2.2 | 1.0924 | 2.2 | 1.2484 | 2.2 | 1.4045 | 2.2 | 1.5605
2.3 | 0.073795 | 2.3 | 0.14759 | 2.3 | 0.29518 | 2.3 | 0.44277 | 2.3 | 0.59036 | 2.3 | 0.73795 | 2.3 | 0.88554 | 2.3 | 1.0331 | 2.3 | 1.1807 | 2.3 | 1.3283 | 2.3 | 1.4759
2.4 | 0.070148 | 2.4 | 0.1403 | 2.4 | 0.28059 | 2.4 | 0.42089 | 2.4 | 0.56118 | 2.4 | 0.70148 | 2.4 | 0.84177 | 2.4 | 0.98207 | 2.4 | 1.1224 | 2.4 | 1.2627 | 2.4 | 1.403
2.5 | 0.066967 | 2.5 | 0.13393 | 2.5 | 0.26787 | 2.5 | 0.4018 | 2.5 | 0.53574 | 2.5 | 0.66967 | 2.5 | 0.80361 | 2.5 | 0.93754 | 2.5 | 1.0715 | 2.5 | 1.2054 | 2.5 | 1.3393
2.55 | 0.065525 | 2.55 | 0.13105 | 2.55 | 0.2621 | 2.55 | 0.39315 | 2.55 | 0.5242 | 2.55 | 0.65525 | 2.55 | 0.7863 | 2.55 | 0.91735 | 2.55 | 1.0484 | 2.55 | 1.1794 | 2.55 | 1.3105
2.6 | 0.064168 | 2.6 | 0.12834 | 2.6 | 0.25667 | 2.6 | 0.38501 | 2.6 | 0.51334 | 2.6 | 0.64168 | 2.6 | 0.77002 | 2.6 | 0.89835 | 2.6 | 1.0267 | 2.6 | 1.155 | 2.6 | 1.2834
2.65 | 0.06289 | 2.65 | 0.12578 | 2.65 | 0.25156 | 2.65 | 0.37734 | 2.65 | 0.50312 | 2.65 | 0.6289 | 2.65 | 0.75468 | 2.65 | 0.88046 | 2.65 | 1.0062 | 2.65 | 1.132 | 2.65 | 1.2578
2.7 | 0.061683 | 2.7 | 0.12337 | 2.7 | 0.24673 | 2.7 | 0.3701 | 2.7 | 0.49346 | 2.7 | 0.61683 | 2.7 | 0.74019 | 2.7 | 0.86356 | 2.7 | 0.98693 | 2.7 | 1.1103 | 2.7 | 1.2337
2.75 | 0.060542 | 2.75 | 0.12108 | 2.75 | 0.24217 | 2.75 | 0.36325 | 2.75 | 0.48433 | 2.75 | 0.60542 | 2.75 | 0.7265 | 2.75 | 0.84758 | 2.75 | 0.96867 | 2.75 | 1.0898 | 2.75 | 1.2108
2.8 | 0.059461 | 2.8 | 0.11892 | 2.8 | 0.23784 | 2.8 | 0.35676 | 2.8 | 0.47568 | 2.8 | 0.59461 | 2.8 | 0.71353 | 2.8 | 0.83245 | 2.8 | 0.95137 | 2.8 | 1.0703 | 2.8 | 1.1892
2.85 | 0.058435 | 2.85 | 0.11687 | 2.85 | 0.23374 | 2.85 | 0.35061 | 2.85 | 0.46748 | 2.85 | 0.58435 | 2.85 | 0.70122 | 2.85 | 0.81809 | 2.85 | 0.93496 | 2.85 | 1.0518 | 2.85 | 1.1687
2.9 | 0.05746 | 2.9 | 0.11492 | 2.9 | 0.22984 | 2.9 | 0.34476 | 2.9 | 0.45968 | 2.9 | 0.5746 | 2.9 | 0.68952 | 2.9 | 0.80444 | 2.9 | 0.91936 | 2.9 | 1.0343 | 2.9 | 1.1492
2.95 | 0.056533 | 2.95 | 0.11307 | 2.95 | 0.22613 | 2.95 | 0.3392 | 2.95 | 0.45226 | 2.95 | 0.56533 | 2.95 | 0.67839 | 2.95 | 0.79146 | 2.95 | 0.90453 | 2.95 | 1.0176 | 2.95 | 1.1307
3 | 0.055649 | 3 | 0.1113 | 3 | 0.2226 | 3 | 0.33389 | 3 | 0.44519 | 3 | 0.55649 | 3 | 0.66779 | 3 | 0.77909 | 3 | 0.89039 | 3 | 1.0017 | 3 | 1.113
3.05 | 0.054806 | 3.05 | 0.10961 | 3.05 | 0.21922 | 3.05 | 0.32884 | 3.05 | 0.43845 | 3.05 | 0.54806 | 3.05 | 0.65767 | 3.05 | 0.76728 | 3.05 | 0.8769 | 3.05 | 0.98651 | 3.05 | 1.0961
3.1 | 0.054001 | 3.1 | 0.108 | 3.1 | 0.216 | 3.1 | 0.324 | 3.1 | 0.432 | 3.1 | 0.54001 | 3.1 | 0.64801 | 3.1 | 0.75601 | 3.1 | 0.86401 | 3.1 | 0.97201 | 3.1 | 1.08
3.15 | 0.05323 | 3.15 | 0.10646 | 3.15 | 0.21292 | 3.15 | 0.31938 | 3.15 | 0.42584 | 3.15 | 0.5323 | 3.15 | 0.63877 | 3.15 | 0.74523 | 3.15 | 0.85169 | 3.15 | 0.95815 | 3.15 | 1.0646
3.2 | 0.052493 | 3.2 | 0.10499 | 3.2 | 0.20997 | 3.2 | 0.31496 | 3.2 | 0.41994 | 3.2 | 0.52493 | 3.2 | 0.62992 | 3.2 | 0.7349 | 3.2 | 0.83989 | 3.2 | 0.94487 | 3.2 | 1.0499
3.25 | 0.051786 | 3.25 | 0.10357 | 3.25 | 0.20715 | 3.25 | 0.31072 | 3.25 | 0.41429 | 3.25 | 0.51786 | 3.25 | 0.62144 | 3.25 | 0.72501 | 3.25 | 0.82858 | 3.25 | 0.93215 | 3.25 | 1.0357
3.3 | 0.051108 | 3.3 | 0.10222 | 3.3 | 0.20443 | 3.3 | 0.30665 | 3.3 | 0.40887 | 3.3 | 0.51108 | 3.3 | 0.6133 | 3.3 | 0.71552 | 3.3 | 0.81773 | 3.3 | 0.91995 | 3.3 | 1.0222
3.35 | 0.050457 | 3.35 | 0.10091 | 3.35 | 0.20183 | 3.35 | 0.30274 | 3.35 | 0.40366 | 3.35 | 0.50457 | 3.35 | 0.60549 | 3.35 | 0.7064 | 3.35 | 0.80732 | 3.35 | 0.90823 | 3.35 | 1.0091
3.4 | 0.049832 | 3.4 | 0.099663 | 3.4 | 0.19933 | 3.4 | 0.29899 | 3.4 | 0.39865 | 3.4 | 0.49832 | 3.4 | 0.59798 | 3.4 | 0.69764 | 3.4 | 0.79731 | 3.4 | 0.89697 | 3.4 | 0.99663
3.45 | 0.04923 | 3.45 | 0.098459 | 3.45 | 0.19692 | 3.45 | 0.29538 | 3.45 | 0.39384 | 3.45 | 0.4923 | 3.45 | 0.59076 | 3.45 | 0.68922 | 3.45 | 0.78768 | 3.45 | 0.88613 | 3.45 | 0.98459
3.5 | 0.04865 | 3.5 | 0.0973 | 3.5 | 0.1946 | 3.5 | 0.2919 | 3.5 | 0.3892 | 3.5 | 0.4865 | 3.5 | 0.5838 | 3.5 | 0.6811 | 3.5 | 0.7784 | 3.5 | 0.8757 | 3.5 | 0.973
3.55 | 0.048092 | 3.55 | 0.096183 | 3.55 | 0.19237 | 3.55 | 0.28855 | 3.55 | 0.38473 | 3.55 | 0.48092 | 3.55 | 0.5771 | 3.55 | 0.67328 | 3.55 | 0.76947 | 3.55 | 0.86565 | 3.55 | 0.96183
3.6 | 0.047553 | 3.6 | 0.095106 | 3.6 | 0.19021 | 3.6 | 0.28532 | 3.6 | 0.38043 | 3.6 | 0.47553 | 3.6 | 0.57064 | 3.6 | 0.66574 | 3.6 | 0.76085 | 3.6 | 0.85596 | 3.6 | 0.95106
3.65 | 0.047034 | 3.65 | 0.094067 | 3.65 | 0.18813 | 3.65 | 0.2822 | 3.65 | 0.37627 | 3.65 | 0.47034 | 3.65 | 0.5644 | 3.65 | 0.65847 | 3.65 | 0.75254 | 3.65 | 0.8466 | 3.65 | 0.94067
3.7 | 0.046532 | 3.7 | 0.093063 | 3.7 | 0.18613 | 3.7 | 0.27919 | 3.7 | 0.37225 | 3.7 | 0.46532 | 3.7 | 0.55838 | 3.7 | 0.65144 | 3.7 | 0.74451 | 3.7 | 0.83757 | 3.7 | 0.93063
3.75 | 0.046047 | 3.75 | 0.092093 | 3.75 | 0.18419 | 3.75 | 0.27628 | 3.75 | 0.36837 | 3.75 | 0.46047 | 3.75 | 0.55256 | 3.75 | 0.64465 | 3.75 | 0.73675 | 3.75 | 0.82884 | 3.75 | 0.92093
3.8 | 0.045578 | 3.8 | 0.091155 | 3.8 | 0.18231 | 3.8 | 0.27347 | 3.8 | 0.36462 | 3.8 | 0.45578 | 3.8 | 0.54693 | 3.8 | 0.63809 | 3.8 | 0.72924 | 3.8 | 0.8204 | 3.8 | 0.91155
3.85 | 0.045124 | 3.85 | 0.090247 | 3.85 | 0.18049 | 3.85 | 0.27074 | 3.85 | 0.36099 | 3.85 | 0.45124 | 3.85 | 0.54148 | 3.85 | 0.63173 | 3.85 | 0.72198 | 3.85 | 0.81223 | 3.85 | 0.90247
3.9 | 0.044684 | 3.9 | 0.089368 | 3.9 | 0.17874 | 3.9 | 0.26811 | 3.9 | 0.35747 | 3.9 | 0.44684 | 3.9 | 0.53621 | 3.9 | 0.62558 | 3.9 | 0.71495 | 3.9 | 0.80432 | 3.9 | 0.89368
3.95 | 0.044258 | 3.95 | 0.088517 | 3.95 | 0.17703 | 3.95 | 0.26555 | 3.95 | 0.35407 | 3.95 | 0.44258 | 3.95 | 0.5311 | 3.95 | 0.61962 | 3.95 | 0.70814 | 3.95 | 0.79665 | 3.95 | 0.88517
4 | 0.043846 | 4 | 0.087692 | 4 | 0.17538 | 4 | 0.26307 | 4 | 0.35077 | 4 | 0.43846 | 4 | 0.52615 | 4 | 0.61384 | 4 | 0.70153 | 4 | 0.78922 | 4 | 0.87692
4.05 | 0.043445 | 4.05 | 0.086891 | 4.05 | 0.17378 | 4.05 | 0.26067 | 4.05 | 0.34756 | 4.05 | 0.43445 | 4.05 | 0.52135 | 4.05 | 0.60824 | 4.05 | 0.69513 | 4.05 | 0.78202 | 4.05 | 0.86891
4.1 | 0.043057 | 4.1 | 0.086114 | 4.1 | 0.17223 | 4.1 | 0.25834 | 4.1 | 0.34446 | 4.1 | 0.43057 | 4.1 | 0.51668 | 4.1 | 0.6028 | 4.1 | 0.68891 | 4.1 | 0.77503 | 4.1 | 0.86114
4.15 | 0.04268 | 4.15 | 0.08536 | 4.15 | 0.17072 | 4.15 | 0.25608 | 4.15 | 0.34144 | 4.15 | 0.4268 | 4.15 | 0.51216 | 4.15 | 0.59752 | 4.15 | 0.68288 | 4.15 | 0.76824 | 4.15 | 0.8536
4.2 | 0.042313 | 4.2 | 0.084627 | 4.2 | 0.16925 | 4.2 | 0.25388 | 4.2 | 0.33851 | 4.2 | 0.42313 | 4.2 | 0.50776 | 4.2 | 0.59239 | 4.2 | 0.67701 | 4.2 | 0.76164 | 4.2 | 0.84627
4.25 | 0.041957 | 4.25 | 0.083915 | 4.25 | 0.16783 | 4.25 | 0.25174 | 4.25 | 0.33566 | 4.25 | 0.41957 | 4.25 | 0.50349 | 4.25 | 0.5874 | 4.25 | 0.67132 | 4.25 | 0.75523 | 4.25 | 0.83915
4.3 | 0.041611 | 4.3 | 0.083222 | 4.3 | 0.16644 | 4.3 | 0.24967 | 4.3 | 0.33289 | 4.3 | 0.41611 | 4.3 | 0.49933 | 4.3 | 0.58255 | 4.3 | 0.66578 | 4.3 | 0.749 | 4.3 | 0.83222
4.35 | 0.041274 | 4.35 | 0.082548 | 4.35 | 0.1651 | 4.35 | 0.24765 | 4.35 | 0.33019 | 4.35 | 0.41274 | 4.35 | 0.49529 | 4.35 | 0.57784 | 4.35 | 0.66039 | 4.35 | 0.74294 | 4.35 | 0.82548
4.4 | 0.040946 | 4.4 | 0.081893 | 4.4 | 0.16379 | 4.4 | 0.24568 | 4.4 | 0.32757 | 4.4 | 0.40946 | 4.4 | 0.49136 | 4.4 | 0.57325 | 4.4 | 0.65514 | 4.4 | 0.73703 | 4.4 | 0.81893
4.45 | 0.040627 | 4.45 | 0.081254 | 4.45 | 0.16251 | 4.45 | 0.24376 | 4.45 | 0.32502 | 4.45 | 0.40627 | 4.45 | 0.48753 | 4.45 | 0.56878 | 4.45 | 0.65003 | 4.45 | 0.73129 | 4.45 | 0.81254
4.5 | 0.040316 | 4.5 | 0.080632 | 4.5 | 0.16126 | 4.5 | 0.2419 | 4.5 | 0.32253 | 4.5 | 0.40316 | 4.5 | 0.48379 | 4.5 | 0.56443 | 4.5 | 0.64506 | 4.5 | 0.72569 | 4.5 | 0.80632
4.55 | 0.040013 | 4.55 | 0.080027 | 4.55 | 0.16005 | 4.55 | 0.24008 | 4.55 | 0.32011 | 4.55 | 0.40013 | 4.55 | 0.48016 | 4.55 | 0.56019 | 4.55 | 0.64021 | 4.55 | 0.72024 | 4.55 | 0.80027
4.6 | 0.039718 | 4.6 | 0.079436 | 4.6 | 0.15887 | 4.6 | 0.23831 | 4.6 | 0.31774 | 4.6 | 0.39718 | 4.6 | 0.47662 | 4.6 | 0.55605 | 4.6 | 0.63549 | 4.6 | 0.71492 | 4.6 | 0.79436
4.65 | 0.03943 | 4.65 | 0.07886 | 4.65 | 0.15772 | 4.65 | 0.23658 | 4.65 | 0.31544 | 4.65 | 0.3943 | 4.65 | 0.47316 | 4.65 | 0.55202 | 4.65 | 0.63088 | 4.65 | 0.70974 | 4.65 | 0.7886
4.7 | 0.039149 | 4.7 | 0.078298 | 4.7 | 0.1566 | 4.7 | 0.23489 | 4.7 | 0.31319 | 4.7 | 0.39149 | 4.7 | 0.46979 | 4.7 | 0.54809 | 4.7 | 0.62638 | 4.7 | 0.70468 | 4.7 | 0.78298
4.75 | 0.038875 | 4.75 | 0.07775 | 4.75 | 0.1555 | 4.75 | 0.23325 | 4.75 | 0.311 | 4.75 | 0.38875 | 4.75 | 0.4665 | 4.75 | 0.54425 | 4.75 | 0.622 | 4.75 | 0.69975 | 4.75 | 0.7775
4.8 | 0.038607 | 4.8 | 0.077214 | 4.8 | 0.15443 | 4.8 | 0.23164 | 4.8 | 0.30886 | 4.8 | 0.38607 | 4.8 | 0.46329 | 4.8 | 0.5405 | 4.8 | 0.61771 | 4.8 | 0.69493 | 4.8 | 0.77214
4.85 | 0.038346 | 4.85 | 0.076691 | 4.85 | 0.15338 | 4.85 | 0.23007 | 4.85 | 0.30677 | 4.85 | 0.38346 | 4.85 | 0.46015 | 4.85 | 0.53684 | 4.85 | 0.61353 | 4.85 | 0.69022 | 4.85 | 0.76691
4.9 | 0.03809 | 4.9 | 0.076181 | 4.9 | 0.15236 | 4.9 | 0.22854 | 4.9 | 0.30472 | 4.9 | 0.3809 | 4.9 | 0.45708 | 4.9 | 0.53326 | 4.9 | 0.60945 | 4.9 | 0.68563 | 4.9 | 0.76181
4.95 | 0.037841 | 4.95 | 0.075682 | 4.95 | 0.15136 | 4.95 | 0.22704 | 4.95 | 0.30273 | 4.95 | 0.37841 | 4.95 | 0.45409 | 4.95 | 0.52977 | 4.95 | 0.60545 | 4.95 | 0.68113 | 4.95 | 0.75682
5 | 0.037597 | 5 | 0.075194 | 5 | 0.15039 | 5 | 0.22558 | 5 | 0.30077 | 5 | 0.37597 | 5 | 0.45116 | 5 | 0.52636 | 5 | 0.60155 | 5 | 0.67674 | 5 | 0.75194
5.05 | 0.037358 | 5.05 | 0.074717 | 5.05 | 0.14943 | 5.05 | 0.22415 | 5.05 | 0.29887 | 5.05 | 0.37358 | 5.05 | 0.4483 | 5.05 | 0.52302 | 5.05 | 0.59773 | 5.05 | 0.67245 | 5.05 | 0.74717
5.1 | 0.037125 | 5.1 | 0.07425 | 5.1 | 0.1485 | 5.1 | 0.22275 | 5.1 | 0.297 | 5.1 | 0.37125 | 5.1 | 0.4455 | 5.1 | 0.51975 | 5.1 | 0.594 | 5.1 | 0.66825 | 5.1 | 0.7425
5.15 | 0.036897 | 5.15 | 0.073793 | 5.15 | 0.14759 | 5.15 | 0.22138 | 5.15 | 0.29517 | 5.15 | 0.36897 | 5.15 | 0.44276 | 5.15 | 0.51655 | 5.15 | 0.59035 | 5.15 | 0.66414 | 5.15 | 0.73793
5.2 | 0.036673 | 5.2 | 0.073347 | 5.2 | 0.14669 | 5.2 | 0.22004 | 5.2 | 0.29339 | 5.2 | 0.36673 | 5.2 | 0.44008 | 5.2 | 0.51343 | 5.2 | 0.58677 | 5.2 | 0.66012 | 5.2 | 0.73347
5.25 | 0.036455 | 5.25 | 0.072909 | 5.25 | 0.14582 | 5.25 | 0.21873 | 5.25 | 0.29164 | 5.25 | 0.36455 | 5.25 | 0.43746 | 5.25 | 0.51037 | 5.25 | 0.58327 | 5.25 | 0.65618 | 5.25 | 0.72909
5.3 | 0.036241 | 5.3 | 0.072481 | 5.3 | 0.14496 | 5.3 | 0.21744 | 5.3 | 0.28992 | 5.3 | 0.36241 | 5.3 | 0.43489 | 5.3 | 0.50737 | 5.3 | 0.57985 | 5.3 | 0.65233 | 5.3 | 0.72481
5.35 | 0.036031 | 5.35 | 0.072062 | 5.35 | 0.14412 | 5.35 | 0.21618 | 5.35 | 0.28825 | 5.35 | 0.36031 | 5.35 | 0.43237 | 5.35 | 0.50443 | 5.35 | 0.57649 | 5.35 | 0.64855 | 5.35 | 0.72062
5.4 | 0.035825 | 5.4 | 0.071651 | 5.4 | 0.1433 | 5.4 | 0.21495 | 5.4 | 0.2866 | 5.4 | 0.35825 | 5.4 | 0.4299 | 5.4 | 0.50155 | 5.4 | 0.5732 | 5.4 | 0.64485 | 5.4 | 0.71651
5.45 | 0.035624 | 5.45 | 0.071248 | 5.45 | 0.1425 | 5.45 | 0.21374 | 5.45 | 0.28499 | 5.45 | 0.35624 | 5.45 | 0.42749 | 5.45 | 0.49873 | 5.45 | 0.56998 | 5.45 | 0.64123 | 5.45 | 0.71248
5.5 | 0.035427 | 5.5 | 0.070853 | 5.5 | 0.14171 | 5.5 | 0.21256 | 5.5 | 0.28341 | 5.5 | 0.35427 | 5.5 | 0.42512 | 5.5 | 0.49597 | 5.5 | 0.56682 | 5.5 | 0.63768 | 5.5 | 0.70853
5.6 | 0.035043 | 5.6 | 0.070086 | 5.6 | 0.14017 | 5.6 | 0.21026 | 5.6 | 0.28035 | 5.6 | 0.35043 | 5.6 | 0.42052 | 5.6 | 0.4906 | 5.6 | 0.56069 | 5.6 | 0.63078 | 5.6 | 0.70086
5.65 | 0.034857 | 5.65 | 0.069714 | 5.65 | 0.13943 | 5.65 | 0.20914 | 5.65 | 0.27886 | 5.65 | 0.34857 | 5.65 | 0.41828 | 5.65 | 0.488 | 5.65 | 0.55771 | 5.65 | 0.62743 | 5.65 | 0.69714
5.7 | 0.034674 | 5.7 | 0.069349 | 5.7 | 0.1387 | 5.7 | 0.20805 | 5.7 | 0.2774 | 5.7 | 0.34674 | 5.7 | 0.41609 | 5.7 | 0.48544 | 5.7 | 0.55479 | 5.7 | 0.62414 | 5.7 | 0.69349
5.75 | 0.034495 | 5.75 | 0.06899 | 5.75 | 0.13798 | 5.75 | 0.20697 | 5.75 | 0.27596 | 5.75 | 0.34495 | 5.75 | 0.41394 | 5.75 | 0.48293 | 5.75 | 0.55192 | 5.75 | 0.62091 | 5.75 | 0.6899
5.8 | 0.034319 | 5.8 | 0.068639 | 5.8 | 0.13728 | 5.8 | 0.20592 | 5.8 | 0.27455 | 5.8 | 0.34319 | 5.8 | 0.41183 | 5.8 | 0.48047 | 5.8 | 0.54911 | 5.8 | 0.61775 | 5.8 | 0.68639
5.85 | 0.034147 | 5.85 | 0.068293 | 5.85 | 0.13659 | 5.85 | 0.20488 | 5.85 | 0.27317 | 5.85 | 0.34147 | 5.85 | 0.40976 | 5.85 | 0.47805 | 5.85 | 0.54635 | 5.85 | 0.61464 | 5.85 | 0.68293
5.9 | 0.033977 | 5.9 | 0.067954 | 5.9 | 0.13591 | 5.9 | 0.20386 | 5.9 | 0.27182 | 5.9 | 0.33977 | 5.9 | 0.40772 | 5.9 | 0.47568 | 5.9 | 0.54363 | 5.9 | 0.61159 | 5.9 | 0.67954
5.95 | 0.03381 | 5.95 | 0.067621 | 5.95 | 0.13524 | 5.95 | 0.20286 | 5.95 | 0.27048 | 5.95 | 0.3381 | 5.95 | 0.40573 | 5.95 | 0.47335 | 5.95 | 0.54097 | 5.95 | 0.60859 | 5.95 | 0.67621
6 | 0.033647 | 6 | 0.067294 | 6 | 0.13459 | 6 | 0.20188 | 6 | 0.26917 | 6 | 0.33647 | 6 | 0.40376 | 6 | 0.47106 | 6 | 0.53835 | 6 | 0.60564 | 6 | 0.67294
6.05 | 0.033486 | 6.05 | 0.066972 | 6.05 | 0.13394 | 6.05 | 0.20092 | 6.05 | 0.26789 | 6.05 | 0.33486 | 6.05 | 0.40183 | 6.05 | 0.46881 | 6.05 | 0.53578 | 6.05 | 0.60275 | 6.05 | 0.66972
6.1 | 0.033328 | 6.1 | 0.066656 | 6.1 | 0.13331 | 6.1 | 0.19997 | 6.1 | 0.26663 | 6.1 | 0.33328 | 6.1 | 0.39994 | 6.1 | 0.46659 | 6.1 | 0.53325 | 6.1 | 0.59991 | 6.1 | 0.66656
6.15 | 0.033173 | 6.15 | 0.066346 | 6.15 | 0.13269 | 6.15 | 0.19904 | 6.15 | 0.26538 | 6.15 | 0.33173 | 6.15 | 0.39807 | 6.15 | 0.46442 | 6.15 | 0.53077 | 6.15 | 0.59711 | 6.15 | 0.66346
6.2 | 0.03302 | 6.2 | 0.06604 | 6.2 | 0.13208 | 6.2 | 0.19812 | 6.2 | 0.26416 | 6.2 | 0.3302 | 6.2 | 0.39624 | 6.2 | 0.46228 | 6.2 | 0.52832 | 6.2 | 0.59436 | 6.2 | 0.6604
6.25 | 0.03287 | 6.25 | 0.06574 | 6.25 | 0.13148 | 6.25 | 0.19722 | 6.25 | 0.26296 | 6.25 | 0.3287 | 6.25 | 0.39444 | 6.25 | 0.46018 | 6.25 | 0.52592 | 6.25 | 0.59166 | 6.25 | 0.6574
6.3 | 0.032723 | 6.3 | 0.065445 | 6.3 | 0.13089 | 6.3 | 0.19634 | 6.3 | 0.26178 | 6.3 | 0.32723 | 6.3 | 0.39267 | 6.3 | 0.45812 | 6.3 | 0.52356 | 6.3 | 0.58901 | 6.3 | 0.65445
6.35 | 0.032577 | 6.35 | 0.065155 | 6.35 | 0.13031 | 6.35 | 0.19546 | 6.35 | 0.26062 | 6.35 | 0.32577 | 6.35 | 0.39093 | 6.35 | 0.45608 | 6.35 | 0.52124 | 6.35 | 0.58639 | 6.35 | 0.65155
6.4 | 0.032435 | 6.4 | 0.064869 | 6.4 | 0.12974 | 6.4 | 0.19461 | 6.4 | 0.25948 | 6.4 | 0.32435 | 6.4 | 0.38922 | 6.4 | 0.45408 | 6.4 | 0.51895 | 6.4 | 0.58382 | 6.4 | 0.64869
6.45 | 0.032294 | 6.45 | 0.064588 | 6.45 | 0.12918 | 6.45 | 0.19376 | 6.45 | 0.25835 | 6.45 | 0.32294 | 6.45 | 0.38753 | 6.45 | 0.45212 | 6.45 | 0.51671 | 6.45 | 0.58129 | 6.45 | 0.64588
6.5 | 0.032156 | 6.5 | 0.064312 | 6.5 | 0.12862 | 6.5 | 0.19294 | 6.5 | 0.25725 | 6.5 | 0.32156 | 6.5 | 0.38587 | 6.5 | 0.45018 | 6.5 | 0.51449 | 6.5 | 0.57881 | 6.5 | 0.64312
6.55 | 0.03202 | 6.55 | 0.06404 | 6.55 | 0.12808 | 6.55 | 0.19212 | 6.55 | 0.25616 | 6.55 | 0.3202 | 6.55 | 0.38424 | 6.55 | 0.44828 | 6.55 | 0.51232 | 6.55 | 0.57636 | 6.55 | 0.6404
6.6 | 0.031886 | 6.6 | 0.063772 | 6.6 | 0.12754 | 6.6 | 0.19132 | 6.6 | 0.25509 | 6.6 | 0.31886 | 6.6 | 0.38263 | 6.6 | 0.4464 | 6.6 | 0.51017 | 6.6 | 0.57395 | 6.6 | 0.63772
6.65 | 0.031754 | 6.65 | 0.063508 | 6.65 | 0.12702 | 6.65 | 0.19052 | 6.65 | 0.25403 | 6.65 | 0.31754 | 6.65 | 0.38105 | 6.65 | 0.44456 | 6.65 | 0.50806 | 6.65 | 0.57157 | 6.65 | 0.63508
6.7 | 0.031624 | 6.7 | 0.063248 | 6.7 | 0.1265 | 6.7 | 0.18974 | 6.7 | 0.25299 | 6.7 | 0.31624 | 6.7 | 0.37949 | 6.7 | 0.44274 | 6.7 | 0.50599 | 6.7 | 0.56923 | 6.7 | 0.63248
6.75 | 0.031496 | 6.75 | 0.062993 | 6.75 | 0.12599 | 6.75 | 0.18898 | 6.75 | 0.25197 | 6.75 | 0.31496 | 6.75 | 0.37796 | 6.75 | 0.44095 | 6.75 | 0.50394 | 6.75 | 0.56693 | 6.75 | 0.62993
6.8 | 0.03137 | 6.8 | 0.062741 | 6.8 | 0.12548 | 6.8 | 0.18822 | 6.8 | 0.25096 | 6.8 | 0.3137 | 6.8 | 0.37644 | 6.8 | 0.43918 | 6.8 | 0.50193 | 6.8 | 0.56467 | 6.8 | 0.62741
6.85 | 0.031246 | 6.85 | 0.062492 | 6.85 | 0.12498 | 6.85 | 0.18748 | 6.85 | 0.24997 | 6.85 | 0.31246 | 6.85 | 0.37495 | 6.85 | 0.43745 | 6.85 | 0.49994 | 6.85 | 0.56243 | 6.85 | 0.62492
6.9 | 0.031124 | 6.9 | 0.062248 | 6.9 | 0.1245 | 6.9 | 0.18674 | 6.9 | 0.24899 | 6.9 | 0.31124 | 6.9 | 0.37349 | 6.9 | 0.43574 | 6.9 | 0.49798 | 6.9 | 0.56023 | 6.9 | 0.62248
6.95 | 0.031004 | 6.95 | 0.062007 | 6.95 | 0.12401 | 6.95 | 0.18602 | 6.95 | 0.24803 | 6.95 | 0.31004 | 6.95 | 0.37204 | 6.95 | 0.43405 | 6.95 | 0.49606 | 6.95 | 0.55806 | 6.95 | 0.62007
7 | 0.030885 | 7 | 0.06177 | 7 | 0.12354 | 7 | 0.18531 | 7 | 0.24708 | 7 | 0.30885 | 7 | 0.37062 | 7 | 0.43239 | 7 | 0.49416 | 7 | 0.55593 | 7 | 0.6177
7.05 | 0.030768 | 7.05 | 0.061536 | 7.05 | 0.12307 | 7.05 | 0.18461 | 7.05 | 0.24614 | 7.05 | 0.30768 | 7.05 | 0.36921 | 7.05 | 0.43075 | 7.05 | 0.49229 | 7.05 | 0.55382 | 7.05 | 0.61536
7.1 | 0.030653 | 7.1 | 0.061305 | 7.1 | 0.12261 | 7.1 | 0.18392 | 7.1 | 0.24522 | 7.1 | 0.30653 | 7.1 | 0.36783 | 7.1 | 0.42914 | 7.1 | 0.49044 | 7.1 | 0.55175 | 7.1 | 0.61305
7.15 | 0.030539 | 7.15 | 0.061078 | 7.15 | 0.12216 | 7.15 | 0.18323 | 7.15 | 0.24431 | 7.15 | 0.30539 | 7.15 | 0.36647 | 7.15 | 0.42754 | 7.15 | 0.48862 | 7.15 | 0.5497 | 7.15 | 0.61078
7.2 | 0.030427 | 7.2 | 0.060854 | 7.2 | 0.12171 | 7.2 | 0.18256 | 7.2 | 0.24341 | 7.2 | 0.30427 | 7.2 | 0.36512 | 7.2 | 0.42597 | 7.2 | 0.48683 | 7.2 | 0.54768 | 7.2 | 0.60854
7.25 | 0.030316 | 7.25 | 0.060632 | 7.25 | 0.12126 | 7.25 | 0.1819 | 7.25 | 0.24253 | 7.25 | 0.30316 | 7.25 | 0.36379 | 7.25 | 0.42443 | 7.25 | 0.48506 | 7.25 | 0.54569 | 7.25 | 0.60632
7.3 | 0.030207 | 7.3 | 0.060414 | 7.3 | 0.12083 | 7.3 | 0.18124 | 7.3 | 0.24166 | 7.3 | 0.30207 | 7.3 | 0.36249 | 7.3 | 0.4229 | 7.3 | 0.48331 | 7.3 | 0.54373 | 7.3 | 0.60414
7.35 | 0.0301 | 7.35 | 0.060199 | 7.35 | 0.1204 | 7.35 | 0.1806 | 7.35 | 0.2408 | 7.35 | 0.301 | 7.35 | 0.3612 | 7.35 | 0.4214 | 7.35 | 0.48159 | 7.35 | 0.54179 | 7.35 | 0.60199
7.4 | 0.029994 | 7.4 | 0.059987 | 7.4 | 0.11997 | 7.4 | 0.17996 | 7.4 | 0.23995 | 7.4 | 0.29994 | 7.4 | 0.35992 | 7.4 | 0.41991 | 7.4 | 0.4799 | 7.4 | 0.53988 | 7.4 | 0.59987
7.45 | 0.029889 | 7.45 | 0.059778 | 7.45 | 0.11956 | 7.45 | 0.17933 | 7.45 | 0.23911 | 7.45 | 0.29889 | 7.45 | 0.35867 | 7.45 | 0.41844 | 7.45 | 0.47822 | 7.45 | 0.538 | 7.45 | 0.59778
7.5 | 0.029786 | 7.5 | 0.059571 | 7.5 | 0.11914 | 7.5 | 0.17871 | 7.5 | 0.23829 | 7.5 | 0.29786 | 7.5 | 0.35743 | 7.5 | 0.417 | 7.5 | 0.47657 | 7.5 | 0.53614 | 7.5 | 0.59571
7.55 | 0.029684 | 7.55 | 0.059368 | 7.55 | 0.11874 | 7.55 | 0.1781 | 7.55 | 0.23747 | 7.55 | 0.29684 | 7.55 | 0.35621 | 7.55 | 0.41557 | 7.55 | 0.47494 | 7.55 | 0.53431 | 7.55 | 0.59368
7.6 | 0.029583 | 7.6 | 0.059166 | 7.6 | 0.11833 | 7.6 | 0.1775 | 7.6 | 0.23667 | 7.6 | 0.29583 | 7.6 | 0.355 | 7.6 | 0.41416 | 7.6 | 0.47333 | 7.6 | 0.5325 | 7.6 | 0.59166
7.65 | 0.029484 | 7.65 | 0.058968 | 7.65 | 0.11794 | 7.65 | 0.1769 | 7.65 | 0.23587 | 7.65 | 0.29484 | 7.65 | 0.35381 | 7.65 | 0.41277 | 7.65 | 0.47174 | 7.65 | 0.53071 | 7.65 | 0.58968
7.7 | 0.029386 | 7.7 | 0.058772 | 7.7 | 0.11754 | 7.7 | 0.17632 | 7.7 | 0.23509 | 7.7 | 0.29386 | 7.7 | 0.35263 | 7.7 | 0.4114 | 7.7 | 0.47018 | 7.7 | 0.52895 | 7.7 | 0.58772
7.75 | 0.029289 | 7.75 | 0.058578 | 7.75 | 0.11716 | 7.75 | 0.17574 | 7.75 | 0.23431 | 7.75 | 0.29289 | 7.75 | 0.35147 | 7.75 | 0.41005 | 7.75 | 0.46863 | 7.75 | 0.52721 | 7.75 | 0.58578
7.8 | 0.029194 | 7.8 | 0.058387 | 7.8 | 0.11677 | 7.8 | 0.17516 | 7.8 | 0.23355 | 7.8 | 0.29194 | 7.8 | 0.35032 | 7.8 | 0.40871 | 7.8 | 0.4671 | 7.8 | 0.52549 | 7.8 | 0.58387
7.85 | 0.029099 | 7.85 | 0.058199 | 7.85 | 0.1164 | 7.85 | 0.1746 | 7.85 | 0.2328 | 7.85 | 0.29099 | 7.85 | 0.34919 | 7.85 | 0.40739 | 7.85 | 0.46559 | 7.85 | 0.52379 | 7.85 | 0.58199
7.9 | 0.029006 | 7.9 | 0.058013 | 7.9 | 0.11603 | 7.9 | 0.17404 | 7.9 | 0.23205 | 7.9 | 0.29006 | 7.9 | 0.34808 | 7.9 | 0.40609 | 7.9 | 0.4641 | 7.9 | 0.52211 | 7.9 | 0.58013
7.95 | 0.028914 | 7.95 | 0.057829 | 7.95 | 0.11566 | 7.95 | 0.17349 | 7.95 | 0.23131 | 7.95 | 0.28914 | 7.95 | 0.34697 | 7.95 | 0.4048 | 7.95 | 0.46263 | 7.95 | 0.52046 | 7.95 | 0.57829
8 | 0.028823 | 8 | 0.057647 | 8 | 0.11529 | 8 | 0.17294 | 8 | 0.23059 | 8 | 0.28823 | 8 | 0.34588 | 8 | 0.40353 | 8 | 0.46118 | 8 | 0.51882 | 8 | 0.57647
8.05 | 0.028734 | 8.05 | 0.057467 | 8.05 | 0.11493 | 8.05 | 0.1724 | 8.05 | 0.22987 | 8.05 | 0.28734 | 8.05 | 0.3448 | 8.05 | 0.40227 | 8.05 | 0.45974 | 8.05 | 0.51721 | 8.05 | 0.57467
8.1 | 0.028645 | 8.1 | 0.05729 | 8.1 | 0.11458 | 8.1 | 0.17187 | 8.1 | 0.22916 | 8.1 | 0.28645 | 8.1 | 0.34374 | 8.1 | 0.40103 | 8.1 | 0.45832 | 8.1 | 0.51561 | 8.1 | 0.5729
8.15 | 0.028558 | 8.15 | 0.057115 | 8.15 | 0.11423 | 8.15 | 0.17135 | 8.15 | 0.22846 | 8.15 | 0.28558 | 8.15 | 0.34269 | 8.15 | 0.39981 | 8.15 | 0.45692 | 8.15 | 0.51404 | 8.15 | 0.57115
8.2 | 0.028471 | 8.2 | 0.056942 | 8.2 | 0.11388 | 8.2 | 0.17083 | 8.2 | 0.22777 | 8.2 | 0.28471 | 8.2 | 0.34165 | 8.2 | 0.39859 | 8.2 | 0.45554 | 8.2 | 0.51248 | 8.2 | 0.56942
8.25 | 0.028385 | 8.25 | 0.056771 | 8.25 | 0.11354 | 8.25 | 0.17031 | 8.25 | 0.22708 | 8.25 | 0.28385 | 8.25 | 0.34063 | 8.25 | 0.3974 | 8.25 | 0.45417 | 8.25 | 0.51094 | 8.25 | 0.56771
8.3 | 0.028301 | 8.3 | 0.056602 | 8.3 | 0.1132 | 8.3 | 0.16981 | 8.3 | 0.22641 | 8.3 | 0.28301 | 8.3 | 0.33961 | 8.3 | 0.39621 | 8.3 | 0.45281 | 8.3 | 0.50942 | 8.3 | 0.56602
8.35 | 0.028217 | 8.35 | 0.056435 | 8.35 | 0.11287 | 8.35 | 0.1693 | 8.35 | 0.22574 | 8.35 | 0.28217 | 8.35 | 0.33861 | 8.35 | 0.39504 | 8.35 | 0.45148 | 8.35 | 0.50791 | 8.35 | 0.56435
8.4 | 0.028135 | 8.4 | 0.05627 | 8.4 | 0.11254 | 8.4 | 0.16881 | 8.4 | 0.22508 | 8.4 | 0.28135 | 8.4 | 0.33762 | 8.4 | 0.39389 | 8.4 | 0.45016 | 8.4 | 0.50643 | 8.4 | 0.5627
8.45 | 0.028053 | 8.45 | 0.056106 | 8.45 | 0.11221 | 8.45 | 0.16832 | 8.45 | 0.22443 | 8.45 | 0.28053 | 8.45 | 0.33664 | 8.45 | 0.39275 | 8.45 | 0.44885 | 8.45 | 0.50496 | 8.45 | 0.56106
8.5 | 0.027973 | 8.5 | 0.055945 | 8.5 | 0.11189 | 8.5 | 0.16784 | 8.5 | 0.22378 | 8.5 | 0.27973 | 8.5 | 0.33567 | 8.5 | 0.39162 | 8.5 | 0.44756 | 8.5 | 0.50351 | 8.5 | 0.55945
8.55 | 0.027893 | 8.55 | 0.055786 | 8.55 | 0.11157 | 8.55 | 0.16736 | 8.55 | 0.22314 | 8.55 | 0.27893 | 8.55 | 0.33471 | 8.55 | 0.3905 | 8.55 | 0.44628 | 8.55 | 0.50207 | 8.55 | 0.55786
8.6 | 0.027814 | 8.6 | 0.055628 | 8.6 | 0.11126 | 8.6 | 0.16688 | 8.6 | 0.22251 | 8.6 | 0.27814 | 8.6 | 0.33377 | 8.6 | 0.38939 | 8.6 | 0.44502 | 8.6 | 0.50065 | 8.6 | 0.55628
8.65 | 0.027736 | 8.65 | 0.055472 | 8.65 | 0.11094 | 8.65 | 0.16642 | 8.65 | 0.22189 | 8.65 | 0.27736 | 8.65 | 0.33283 | 8.65 | 0.3883 | 8.65 | 0.44377 | 8.65 | 0.49925 | 8.65 | 0.55472
8.7 | 0.027659 | 8.7 | 0.055318 | 8.7 | 0.11064 | 8.7 | 0.16595 | 8.7 | 0.22127 | 8.7 | 0.27659 | 8.7 | 0.33191 | 8.7 | 0.38722 | 8.7 | 0.44254 | 8.7 | 0.49786 | 8.7 | 0.55318
8.75 | 0.027582 | 8.75 | 0.055165 | 8.75 | 0.11033 | 8.75 | 0.16549 | 8.75 | 0.22066 | 8.75 | 0.27582 | 8.75 | 0.33099 | 8.75 | 0.38615 | 8.75 | 0.44132 | 8.75 | 0.49648 | 8.75 | 0.55165
8.8 | 0.027507 | 8.8 | 0.055014 | 8.8 | 0.11003 | 8.8 | 0.16504 | 8.8 | 0.22006 | 8.8 | 0.27507 | 8.8 | 0.33008 | 8.8 | 0.3851 | 8.8 | 0.44011 | 8.8 | 0.49513 | 8.8 | 0.55014
8.85 | 0.027432 | 8.85 | 0.054865 | 8.85 | 0.10973 | 8.85 | 0.16459 | 8.85 | 0.21946 | 8.85 | 0.27432 | 8.85 | 0.32919 | 8.85 | 0.38405 | 8.85 | 0.43892 | 8.85 | 0.49378 | 8.85 | 0.54865
8.9 | 0.027359 | 8.9 | 0.054717 | 8.9 | 0.10943 | 8.9 | 0.16415 | 8.9 | 0.21887 | 8.9 | 0.27359 | 8.9 | 0.3283 | 8.9 | 0.38302 | 8.9 | 0.43774 | 8.9 | 0.49245 | 8.9 | 0.54717
8.95 | 0.027286 | 8.95 | 0.054571 | 8.95 | 0.10914 | 8.95 | 0.16371 | 8.95 | 0.21828 | 8.95 | 0.27286 | 8.95 | 0.32743 | 8.95 | 0.382 | 8.95 | 0.43657 | 8.95 | 0.49114 | 8.95 | 0.54571
9 | 0.027213 | 9 | 0.054427 | 9 | 0.10885 | 9 | 0.16328 | 9 | 0.21771 | 9 | 0.27213 | 9 | 0.32656 | 9 | 0.38099 | 9 | 0.43541 | 9 | 0.48984 | 9 | 0.54427
9.05 | 0.027142 | 9.05 | 0.054284 | 9.05 | 0.10857 | 9.05 | 0.16285 | 9.05 | 0.21713 | 9.05 | 0.27142 | 9.05 | 0.3257 | 9.05 | 0.37999 | 9.05 | 0.43427 | 9.05 | 0.48855 | 9.05 | 0.54284
9.1 | 0.027071 | 9.1 | 0.054142 | 9.1 | 0.10828 | 9.1 | 0.16243 | 9.1 | 0.21657 | 9.1 | 0.27071 | 9.1 | 0.32485 | 9.1 | 0.37899 | 9.1 | 0.43314 | 9.1 | 0.48728 | 9.1 | 0.54142
9.15 | 0.027001 | 9.15 | 0.054002 | 9.15 | 0.108 | 9.15 | 0.16201 | 9.15 | 0.21601 | 9.15 | 0.27001 | 9.15 | 0.32401 | 9.15 | 0.37801 | 9.15 | 0.43202 | 9.15 | 0.48602 | 9.15 | 0.54002
9.2 | 0.026932 | 9.2 | 0.053863 | 9.2 | 0.10773 | 9.2 | 0.16159 | 9.2 | 0.21545 | 9.2 | 0.26932 | 9.2 | 0.32318 | 9.2 | 0.37704 | 9.2 | 0.43091 | 9.2 | 0.48477 | 9.2 | 0.53863
9.25 | 0.026863 | 9.25 | 0.053726 | 9.25 | 0.10745 | 9.25 | 0.16118 | 9.25 | 0.21491 | 9.25 | 0.26863 | 9.25 | 0.32236 | 9.25 | 0.37608 | 9.25 | 0.42981 | 9.25 | 0.48354 | 9.25 | 0.53726
9.3 | 0.026795 | 9.3 | 0.053591 | 9.3 | 0.10718 | 9.3 | 0.16077 | 9.3 | 0.21436 | 9.3 | 0.26795 | 9.3 | 0.32154 | 9.3 | 0.37513 | 9.3 | 0.42872 | 9.3 | 0.48232 | 9.3 | 0.53591
9.35 | 0.026728 | 9.35 | 0.053456 | 9.35 | 0.10691 | 9.35 | 0.16037 | 9.35 | 0.21382 | 9.35 | 0.26728 | 9.35 | 0.32074 | 9.35 | 0.37419 | 9.35 | 0.42765 | 9.35 | 0.48111 | 9.35 | 0.53456
9.4 | 0.026662 | 9.4 | 0.053323 | 9.4 | 0.10665 | 9.4 | 0.15997 | 9.4 | 0.21329 | 9.4 | 0.26662 | 9.4 | 0.31994 | 9.4 | 0.37326 | 9.4 | 0.42659 | 9.4 | 0.47991 | 9.4 | 0.53323
9.45 | 0.026596 | 9.45 | 0.053192 | 9.45 | 0.10638 | 9.45 | 0.15957 | 9.45 | 0.21277 | 9.45 | 0.26596 | 9.45 | 0.31915 | 9.45 | 0.37234 | 9.45 | 0.42553 | 9.45 | 0.47872 | 9.45 | 0.53192
9.5 | 0.026531 | 9.5 | 0.053061 | 9.5 | 0.10612 | 9.5 | 0.15918 | 9.5 | 0.21224 | 9.5 | 0.26531 | 9.5 | 0.31837 | 9.5 | 0.37143 | 9.5 | 0.42449 | 9.5 | 0.47755 | 9.5 | 0.53061
9.55 | 0.026466 | 9.55 | 0.052932 | 9.55 | 0.10586 | 9.55 | 0.1588 | 9.55 | 0.21173 | 9.55 | 0.26466 | 9.55 | 0.31759 | 9.55 | 0.37052 | 9.55 | 0.42346 | 9.55 | 0.47639 | 9.55 | 0.52932
9.6 | 0.026402 | 9.6 | 0.052804 | 9.6 | 0.10561 | 9.6 | 0.15841 | 9.6 | 0.21122 | 9.6 | 0.26402 | 9.6 | 0.31683 | 9.6 | 0.36963 | 9.6 | 0.42243 | 9.6 | 0.47524 | 9.6 | 0.52804
9.65 | 0.026339 | 9.65 | 0.052678 | 9.65 | 0.10536 | 9.65 | 0.15803 | 9.65 | 0.21071 | 9.65 | 0.26339 | 9.65 | 0.31607 | 9.65 | 0.36874 | 9.65 | 0.42142 | 9.65 | 0.4741 | 9.65 | 0.52678
9.7 | 0.026276 | 9.7 | 0.052552 | 9.7 | 0.1051 | 9.7 | 0.15766 | 9.7 | 0.21021 | 9.7 | 0.26276 | 9.7 | 0.31531 | 9.7 | 0.36787 | 9.7 | 0.42042 | 9.7 | 0.47297 | 9.7 | 0.52552
9.75 | 0.026214 | 9.75 | 0.052428 | 9.75 | 0.10486 | 9.75 | 0.15728 | 9.75 | 0.20971 | 9.75 | 0.26214 | 9.75 | 0.31457 | 9.75 | 0.367 | 9.75 | 0.41943 | 9.75 | 0.47185 | 9.75 | 0.52428
9.8 | 0.026153 | 9.8 | 0.052305 | 9.8 | 0.10461 | 9.8 | 0.15692 | 9.8 | 0.20922 | 9.8 | 0.26153 | 9.8 | 0.31383 | 9.8 | 0.36614 | 9.8 | 0.41844 | 9.8 | 0.47075 | 9.8 | 0.52305
9.85 | 0.026092 | 9.85 | 0.052184 | 9.85 | 0.10437 | 9.85 | 0.15655 | 9.85 | 0.20873 | 9.85 | 0.26092 | 9.85 | 0.3131 | 9.85 | 0.36529 | 9.85 | 0.41747 | 9.85 | 0.46965 | 9.85 | 0.52184
9.9 | 0.026032 | 9.9 | 0.052063 | 9.9 | 0.10413 | 9.9 | 0.15619 | 9.9 | 0.20825 | 9.9 | 0.26032 | 9.9 | 0.31238 | 9.9 | 0.36444 | 9.9 | 0.4165 | 9.9 | 0.46857 | 9.9 | 0.52063
9.95 | 0.025972 | 9.95 | 0.051944 | 9.95 | 0.10389 | 9.95 | 0.15583 | 9.95 | 0.20777 | 9.95 | 0.25972 | 9.95 | 0.31166 | 9.95 | 0.3636 | 9.95 | 0.41555 | 9.95 | 0.46749 | 9.95 | 0.51944
10 | 0.025913 | 10 | 0.051825 | 10 | 0.10365 | 10 | 0.15548 | 10 | 0.2073 | 10 | 0.25913 | 10 | 0.31095 | 10 | 0.36278 | 10 | 0.4146 | 10 | 0.46643 | 10 | 0.51825
10.25 | 0.025625 | 10.25 | 0.05125 | 10.25 | 0.1025 | 10.25 | 0.15375 | 10.25 | 0.205 | 10.25 | 0.25625 | 10.25 | 0.3075 | 10.25 | 0.35875 | 10.25 | 0.41 | 10.25 | 0.46125 | 10.25 | 0.5125
10.5 | 0.02535 | 10.5 | 0.0507 | 10.5 | 0.1014 | 10.5 | 0.1521 | 10.5 | 0.2028 | 10.5 | 0.2535 | 10.5 | 0.3042 | 10.5 | 0.3549 | 10.5 | 0.4056 | 10.5 | 0.4563 | 10.5 | 0.507
10.75 | 0.025087 | 10.75 | 0.050173 | 10.75 | 0.10035 | 10.75 | 0.15052 | 10.75 | 0.20069 | 10.75 | 0.25087 | 10.75 | 0.30104 | 10.75 | 0.35121 | 10.75 | 0.40139 | 10.75 | 0.45156 | 10.75 | 0.50173
11 | 0.024835 | 11 | 0.049669 | 11 | 0.099338 | 11 | 0.14901 | 11 | 0.19868 | 11 | 0.24835 | 11 | 0.29801 | 11 | 0.34768 | 11 | 0.39735 | 11 | 0.44702 | 11 | 0.49669
11.25 | 0.024593 | 11.25 | 0.049185 | 11.25 | 0.098371 | 11.25 | 0.14756 | 11.25 | 0.19674 | 11.25 | 0.24593 | 11.25 | 0.29511 | 11.25 | 0.3443 | 11.25 | 0.39348 | 11.25 | 0.44267 | 11.25 | 0.49185
11.5 | 0.02436 | 11.5 | 0.048721 | 11.5 | 0.097442 | 11.5 | 0.14616 | 11.5 | 0.19488 | 11.5 | 0.2436 | 11.5 | 0.29233 | 11.5 | 0.34105 | 11.5 | 0.38977 | 11.5 | 0.43849 | 11.5 | 0.48721
11.75 | 0.024137 | 11.75 | 0.048275 | 11.75 | 0.096549 | 11.75 | 0.14482 | 11.75 | 0.1931 | 11.75 | 0.24137 | 11.75 | 0.28965 | 11.75 | 0.33792 | 11.75 | 0.3862 | 11.75 | 0.43447 | 11.75 | 0.48275
12 | 0.023923 | 12 | 0.047845 | 12 | 0.09569 | 12 | 0.14354 | 12 | 0.19138 | 12 | 0.23923 | 12 | 0.28707 | 12 | 0.33492 | 12 | 0.38276 | 12 | 0.43061 | 12 | 0.47845
12.25 | 0.023716 | 12.25 | 0.047431 | 12.25 | 0.094863 | 12.25 | 0.14229 | 12.25 | 0.18973 | 12.25 | 0.23716 | 12.25 | 0.28459 | 12.25 | 0.33202 | 12.25 | 0.37945 | 12.25 | 0.42688 | 12.25 | 0.47431
12.5 | 0.023516 | 12.5 | 0.047033 | 12.5 | 0.094066 | 12.5 | 0.1411 | 12.5 | 0.18813 | 12.5 | 0.23516 | 12.5 | 0.2822 | 12.5 | 0.32923 | 12.5 | 0.37626 | 12.5 | 0.42329 | 12.5 | 0.47033
12.75 | 0.023324 | 12.75 | 0.046648 | 12.75 | 0.093296 | 12.75 | 0.13994 | 12.75 | 0.18659 | 12.75 | 0.23324 | 12.75 | 0.27989 | 12.75 | 0.32654 | 12.75 | 0.37318 | 12.75 | 0.41983 | 12.75 | 0.46648
13 | 0.023138 | 13 | 0.046277 | 13 | 0.092553 | 13 | 0.13883 | 13 | 0.18511 | 13 | 0.23138 | 13 | 0.27766 | 13 | 0.32394 | 13 | 0.37021 | 13 | 0.41649 | 13 | 0.46277
13.25 | 0.022959 | 13.25 | 0.045918 | 13.25 | 0.091835 | 13.25 | 0.13775 | 13.25 | 0.18367 | 13.25 | 0.22959 | 13.25 | 0.27551 | 13.25 | 0.32142 | 13.25 | 0.36734 | 13.25 | 0.41326 | 13.25 | 0.45918
13.5 | 0.022785 | 13.5 | 0.045571 | 13.5 | 0.091141 | 13.5 | 0.13671 | 13.5 | 0.18228 | 13.5 | 0.22785 | 13.5 | 0.27342 | 13.5 | 0.31899 | 13.5 | 0.36456 | 13.5 | 0.41014 | 13.5 | 0.45571
13.75 | 0.022617 | 13.75 | 0.045235 | 13.75 | 0.090469 | 13.75 | 0.1357 | 13.75 | 0.18094 | 13.75 | 0.22617 | 13.75 | 0.27141 | 13.75 | 0.31664 | 13.75 | 0.36188 | 13.75 | 0.40711 | 13.75 | 0.45235
14 | 0.022455 | 14 | 0.044909 | 14 | 0.089819 | 14 | 0.13473 | 14 | 0.17964 | 14 | 0.22455 | 14 | 0.26946 | 14 | 0.31437 | 14 | 0.35927 | 14 | 0.40418 | 14 | 0.44909
14.25 | 0.022297 | 14.25 | 0.044594 | 14.25 | 0.089188 | 14.25 | 0.13378 | 14.25 | 0.17838 | 14.25 | 0.22297 | 14.25 | 0.26756 | 14.25 | 0.31216 | 14.25 | 0.35675 | 14.25 | 0.40135 | 14.25 | 0.44594
14.5 | 0.022144 | 14.5 | 0.044288 | 14.5 | 0.088577 | 14.5 | 0.13287 | 14.5 | 0.17715 | 14.5 | 0.22144 | 14.5 | 0.26573 | 14.5 | 0.31002 | 14.5 | 0.35431 | 14.5 | 0.3986 | 14.5 | 0.44288
14.75 | 0.021996 | 14.75 | 0.043992 | 14.75 | 0.087984 | 14.75 | 0.13198 | 14.75 | 0.17597 | 14.75 | 0.21996 | 14.75 | 0.26395 | 14.75 | 0.30794 | 14.75 | 0.35193 | 14.75 | 0.39593 | 14.75 | 0.43992
15 | 0.021852 | 15 | 0.043704 | 15 | 0.087408 | 15 | 0.13111 | 15 | 0.17482 | 15 | 0.21852 | 15 | 0.26222 | 15 | 0.30593 | 15 | 0.34963 | 15 | 0.39333 | 15 | 0.43704
15.5 | 0.021576 | 15.5 | 0.043152 | 15.5 | 0.086304 | 15.5 | 0.12946 | 15.5 | 0.17261 | 15.5 | 0.21576 | 15.5 | 0.25891 | 15.5 | 0.30206 | 15.5 | 0.34522 | 15.5 | 0.38837 | 15.5 | 0.43152
16 | 0.021315 | 16 | 0.04263 | 16 | 0.085261 | 16 | 0.12789 | 16 | 0.17052 | 16 | 0.21315 | 16 | 0.25578 | 16 | 0.29841 | 16 | 0.34104 | 16 | 0.38367 | 16 | 0.4263
16.5 | 0.021068 | 16.5 | 0.042136 | 16.5 | 0.084272 | 16.5 | 0.12641 | 16.5 | 0.16854 | 16.5 | 0.21068 | 16.5 | 0.25282 | 16.5 | 0.29495 | 16.5 | 0.33709 | 16.5 | 0.37922 | 16.5 | 0.42136
17 | 0.020833 | 17 | 0.041667 | 17 | 0.083333 | 17 | 0.125 | 17 | 0.16667 | 17 | 0.20833 | 17 | 0.25 | 17 | 0.29167 | 17 | 0.33333 | 17 | 0.375 | 17 | 0.41667
17.5 | 0.02061 | 17.5 | 0.04122 | 17.5 | 0.082441 | 17.5 | 0.12366 | 17.5 | 0.16488 | 17.5 | 0.2061 | 17.5 | 0.24732 | 17.5 | 0.28854 | 17.5 | 0.32976 | 17.5 | 0.37098 | 17.5 | 0.4122
18 | 0.020398 | 18 | 0.040795 | 18 | 0.08159 | 18 | 0.12239 | 18 | 0.16318 | 18 | 0.20398 | 18 | 0.24477 | 18 | 0.28557 | 18 | 0.32636 | 18 | 0.36716 | 18 | 0.40795
18.5 | 0.020195 | 18.5 | 0.04039 | 18.5 | 0.080779 | 18.5 | 0.12117 | 18.5 | 0.16156 | 18.5 | 0.20195 | 18.5 | 0.24234 | 18.5 | 0.28273 | 18.5 | 0.32312 | 18.5 | 0.36351 | 18.5 | 0.4039
19 | 0.020001 | 19 | 0.040002 | 19 | 0.080004 | 19 | 0.12001 | 19 | 0.16001 | 19 | 0.20001 | 19 | 0.24001 | 19 | 0.28001 | 19 | 0.32002 | 19 | 0.36002 | 19 | 0.40002
19.5 | 0.019816 | 19.5 | 0.039631 | 19.5 | 0.079262 | 19.5 | 0.11889 | 19.5 | 0.15852 | 19.5 | 0.19816 | 19.5 | 0.23779 | 19.5 | 0.27742 | 19.5 | 0.31705 | 19.5 | 0.35668 | 19.5 | 0.39631
20 | 0.019638 | 20 | 0.039276 | 20 | 0.078552 | 20 | 0.11783 | 20 | 0.1571 | 20 | 0.19638 | 20 | 0.23566 | 20 | 0.27493 | 20 | 0.31421 | 20 | 0.35348 | 20 | 0.39276
20.5 | 0.019468 | 20.5 | 0.038935 | 20.5 | 0.07787 | 20.5 | 0.11681 | 20.5 | 0.15574 | 20.5 | 0.19468 | 20.5 | 0.23361 | 20.5 | 0.27255 | 20.5 | 0.31148 | 20.5 | 0.35042 | 20.5 | 0.38935
21 | 0.019304 | 21 | 0.038608 | 21 | 0.077216 | 21 | 0.11582 | 21 | 0.15443 | 21 | 0.19304 | 21 | 0.23165 | 21 | 0.27026 | 21 | 0.30886 | 21 | 0.34747 | 21 | 0.38608
21.5 | 0.019147 | 21.5 | 0.038294 | 21.5 | 0.076587 | 21.5 | 0.11488 | 21.5 | 0.15317 | 21.5 | 0.19147 | 21.5 | 0.22976 | 21.5 | 0.26806 | 21.5 | 0.30635 | 21.5 | 0.34464 | 21.5 | 0.38294
22 | 0.018995 | 22 | 0.037991 | 22 | 0.075982 | 22 | 0.11397 | 22 | 0.15196 | 22 | 0.18995 | 22 | 0.22795 | 22 | 0.26594 | 22 | 0.30393 | 22 | 0.34192 | 22 | 0.37991
22.5 | 0.01885 | 22.5 | 0.037699 | 22.5 | 0.075399 | 22.5 | 0.1131 | 22.5 | 0.1508 | 22.5 | 0.1885 | 22.5 | 0.2262 | 22.5 | 0.2639 | 22.5 | 0.3016 | 22.5 | 0.33929 | 22.5 | 0.37699
23 | 0.018709 | 23 | 0.037418 | 23 | 0.074837 | 23 | 0.11226 | 23 | 0.14967 | 23 | 0.18709 | 23 | 0.22451 | 23 | 0.26193 | 23 | 0.29935 | 23 | 0.33677 | 23 | 0.37418
23.5 | 0.018574 | 23.5 | 0.037147 | 23.5 | 0.074294 | 23.5 | 0.11144 | 23.5 | 0.14859 | 23.5 | 0.18574 | 23.5 | 0.22288 | 23.5 | 0.26003 | 23.5 | 0.29718 | 23.5 | 0.33432 | 23.5 | 0.37147
24 | 0.018443 | 24 | 0.036885 | 24 | 0.07377 | 24 | 0.11066 | 24 | 0.14754 | 24 | 0.18443 | 24 | 0.22131 | 24 | 0.2582 | 24 | 0.29508 | 24 | 0.33197 | 24 | 0.36885
24.5 | 0.018316 | 24.5 | 0.036632 | 24.5 | 0.073264 | 24.5 | 0.1099 | 24.5 | 0.14653 | 24.5 | 0.18316 | 24.5 | 0.21979 | 24.5 | 0.25642 | 24.5 | 0.29306 | 24.5 | 0.32969 | 24.5 | 0.36632
25 | 0.018194 | 25 | 0.036387 | 25 | 0.072774 | 25 | 0.10916 | 25 | 0.14555 | 25 | 0.18194 | 25 | 0.21832 | 25 | 0.25471 | 25 | 0.2911 | 25 | 0.32748 | 25 | 0.36387
25.5 | 0.018075 | 25.5 | 0.03615 | 25.5 | 0.0723 | 25.5 | 0.10845 | 25.5 | 0.1446 | 25.5 | 0.18075 | 25.5 | 0.2169 | 25.5 | 0.25305 | 25.5 | 0.2892 | 25.5 | 0.32535 | 25.5 | 0.3615
26 | 0.01796 | 26 | 0.03592 | 26 | 0.07184 | 26 | 0.10776 | 26 | 0.14368 | 26 | 0.1796 | 26 | 0.21552 | 26 | 0.25144 | 26 | 0.28736 | 26 | 0.32328 | 26 | 0.3592
26.5 | 0.017849 | 26.5 | 0.035698 | 26.5 | 0.071395 | 26.5 | 0.10709 | 26.5 | 0.14279 | 26.5 | 0.17849 | 26.5 | 0.21419 | 26.5 | 0.24988 | 26.5 | 0.28558 | 26.5 | 0.32128 | 26.5 | 0.35698
27 | 0.017741 | 27 | 0.035482 | 27 | 0.070963 | 27 | 0.10644 | 27 | 0.14193 | 27 | 0.17741 | 27 | 0.21289 | 27 | 0.24837 | 27 | 0.28385 | 27 | 0.31933 | 27 | 0.35482
27.5 | 0.017636 | 27.5 | 0.035272 | 27.5 | 0.070544 | 27.5 | 0.10582 | 27.5 | 0.14109 | 27.5 | 0.17636 | 27.5 | 0.21163 | 27.5 | 0.2469 | 27.5 | 0.28217 | 27.5 | 0.31745 | 27.5 | 0.35272
28 | 0.017534 | 28 | 0.035068 | 28 | 0.070136 | 28 | 0.1052 | 28 | 0.14027 | 28 | 0.17534 | 28 | 0.21041 | 28 | 0.24548 | 28 | 0.28055 | 28 | 0.31561 | 28 | 0.35068
28.5 | 0.017435 | 28.5 | 0.03487 | 28.5 | 0.069741 | 28.5 | 0.10461 | 28.5 | 0.13948 | 28.5 | 0.17435 | 28.5 | 0.20922 | 28.5 | 0.24409 | 28.5 | 0.27896 | 28.5 | 0.31383 | 28.5 | 0.3487
29 | 0.017339 | 29 | 0.034678 | 29 | 0.069356 | 29 | 0.10403 | 29 | 0.13871 | 29 | 0.17339 | 29 | 0.20807 | 29 | 0.24275 | 29 | 0.27742 | 29 | 0.3121 | 29 | 0.34678
29.5 | 0.017245 | 29.5 | 0.034491 | 29.5 | 0.068981 | 29.5 | 0.10347 | 29.5 | 0.13796 | 29.5 | 0.17245 | 29.5 | 0.20694 | 29.5 | 0.24143 | 29.5 | 0.27593 | 29.5 | 0.31042 | 29.5 | 0.34491
30 | 0.017154 | 30 | 0.034308 | 30 | 0.068617 | 30 | 0.10293 | 30 | 0.13723 | 30 | 0.17154 | 30 | 0.20585 | 30 | 0.24016 | 30 | 0.27447 | 30 | 0.30878 | 30 | 0.34308
31 | 0.017154 | 31 | 0.034308 | 31 | 0.068617 | 31 | 0.10293 | 31 | 0.13723 | 31 | 0.17154 | 31 | 0.20585 | 31 | 0.24016 | 31 | 0.27447 | 31 | 0.30878 | 31 | 0.34308
32 | 0.017154 | 32 | 0.034308 | 32 | 0.068617 | 32 | 0.10293 | 32 | 0.13723 | 32 | 0.17154 | 32 | 0.20585 | 32 | 0.24016 | 32 | 0.27447 | 32 | 0.30878 | 32 | 0.34308
33 | 0.017154 | 33 | 0.034308 | 33 | 0.068617 | 33 | 0.10293 | 33 | 0.13723 | 33 | 0.17154 | 33 | 0.20585 | 33 | 0.24016 | 33 | 0.27447 | 33 | 0.30878 | 33 | 0.34308
34 | 0.017154 | 34 | 0.034308 | 34 | 0.068617 | 34 | 0.10293 | 34 | 0.13723 | 34 | 0.17154 | 34 | 0.20585 | 34 | 0.24016 | 34 | 0.27447 | 34 | 0.30878 | 34 | 0.34308
35 | 0.017154 | 35 | 0.034308 | 35 | 0.068617 | 35 | 0.10293 | 35 | 0.13723 | 35 | 0.17154 | 35 | 0.20585 | 35 | 0.24016 | 35 | 0.27447 | 35 | 0.30878 | 35 | 0.34308
36 | 0.017154 | 36 | 0.034308 | 36 | 0.068617 | 36 | 0.10293 | 36 | 0.13723 | 36 | 0.17154 | 36 | 0.20585 | 36 | 0.24016 | 36 | 0.27447 | 36 | 0.30878 | 36 | 0.34308
37 | 0.017154 | 37 | 0.034308 | 37 | 0.068617 | 37 | 0.10293 | 37 | 0.13723 | 37 | 0.17154 | 37 | 0.20585 | 37 | 0.24016 | 37 | 0.27447 | 37 | 0.30878 | 37 | 0.34308
38 | 0.017154 | 38 | 0.034308 | 38 | 0.068617 | 38 | 0.10293 | 38 | 0.13723 | 38 | 0.17154 | 38 | 0.20585 | 38 | 0.24016 | 38 | 0.27447 | 38 | 0.30878 | 38 | 0.34308
39 | 0.017154 | 39 | 0.034308 | 39 | 0.068617 | 39 | 0.10293 | 39 | 0.13723 | 39 | 0.17154 | 39 | 0.20585 | 39 | 0.24016 | 39 | 0.27447 | 39 | 0.30878 | 39 | 0.34308
40 | 0.017154 | 40 | 0.034308 | 40 | 0.068617 | 40 | 0.10293 | 40 | 0.13723 | 40 | 0.17154 | 40 | 0.20585 | 40 | 0.24016 | 40 | 0.27447 | 40 | 0.30878 | 40 | 0.34308
41 | 0.017154 | 41 | 0.034308 | 41 | 0.068617 | 41 | 0.10293 | 41 | 0.13723 | 41 | 0.17154 | 41 | 0.20585 | 41 | 0.24016 | 41 | 0.27447 | 41 | 0.30878 | 41 | 0.34308
42 | 0.017154 | 42 | 0.034308 | 42 | 0.068617 | 42 | 0.10293 | 42 | 0.13723 | 42 | 0.17154 | 42 | 0.20585 | 42 | 0.24016 | 42 | 0.27447 | 42 | 0.30878 | 42 | 0.34308
43 | 0.017154 | 43 | 0.034308 | 43 | 0.068617 | 43 | 0.10293 | 43 | 0.13723 | 43 | 0.17154 | 43 | 0.20585 | 43 | 0.24016 | 43 | 0.27447 | 43 | 0.30878 | 43 | 0.34308
44 | 0.017154 | 44 | 0.034308 | 44 | 0.068617 | 44 | 0.10293 | 44 | 0.13723 | 44 | 0.17154 | 44 | 0.20585 | 44 | 0.24016 | 44 | 0.27447 | 44 | 0.30878 | 44 | 0.34308
45 | 0.017154 | 45 | 0.034308 | 45 | 0.068617 | 45 | 0.10293 | 45 | 0.13723 | 45 | 0.17154 | 45 | 0.20585 | 45 | 0.24016 | 45 | 0.27447 | 45 | 0.30878 | 45 | 0.34308
46 | 0.017154 | 46 | 0.034308 | 46 | 0.068617 | 46 | 0.10293 | 46 | 0.13723 | 46 | 0.17154 | 46 | 0.20585 | 46 | 0.24016 | 46 | 0.27447 | 46 | 0.30878 | 46 | 0.34308
47 | 0.017154 | 47 | 0.034308 | 47 | 0.068617 | 47 | 0.10293 | 47 | 0.13723 | 47 | 0.17154 | 47 | 0.20585 | 47 | 0.24016 | 47 | 0.27447 | 47 | 0.30878 | 47 | 0.34308
48 | 0.017154 | 48 | 0.034308 | 48 | 0.068617 | 48 | 0.10293 | 48 | 0.13723 | 48 | 0.17154 | 48 | 0.20585 | 48 | 0.24016 | 48 | 0.27447 | 48 | 0.30878 | 48 | 0.34308
49 | 0.017154 | 49 | 0.034308 | 49 | 0.068617 | 49 | 0.10293 | 49 | 0.13723 | 49 | 0.17154 | 49 | 0.20585 | 49 | 0.24016 | 49 | 0.27447 | 49 | 0.30878 | 49 | 0.34308
50 | 0.017154 | 50 | 0.034308 | 50 | 0.068617 | 50 | 0.10293 | 50 | 0.13723 | 50 | 0.17154 | 50 | 0.20585 | 50 | 0.24016 | 50 | 0.27447 | 50 | 0.30878 | 50 | 0.34308
55 | 0.017154 | 55 | 0.034308 | 55 | 0.068617 | 55 | 0.10293 | 55 | 0.13723 | 55 | 0.17154 | 55 | 0.20585 | 55 | 0.24016 | 55 | 0.27447 | 55 | 0.30878 | 55 | 0.34308
60 | 0.017154 | 60 | 0.034308 | 60 | 0.068617 | 60 | 0.10293 | 60 | 0.13723 | 60 | 0.17154 | 60 | 0.20585 | 60 | 0.24016 | 60 | 0.27447 | 60 | 0.30878 | 60 | 0.34308
65 | 0.017154 | 65 | 0.034308 | 65 | 0.068617 | 65 | 0.10293 | 65 | 0.13723 | 65 | 0.17154 | 65 | 0.20585 | 65 | 0.24016 | 65 | 0.27447 | 65 | 0.30878 | 65 | 0.34308
70 | 0.017154 | 70 | 0.034308 | 70 | 0.068617 | 70 | 0.10293 | 70 | 0.13723 | 70 | 0.17154 | 70 | 0.20585 | 70 | 0.24016 | 70 | 0.27447 | 70 | 0.30878 | 70 | 0.34308
75 | 0.017154 | 75 | 0.034308 | 75 | 0.068617 | 75 | 0.10293 | 75 | 0.13723 | 75 | 0.17154 | 75 | 0.20585 | 75 | 0.24016 | 75 | 0.27447 | 75 | 0.30878 | 75 | 0.34308
80 | 0.017154 | 80 | 0.034308 | 80 | 0.068617 | 80 | 0.10293 | 80 | 0.13723 | 80 | 0.17154 | 80 | 0.20585 | 80 | 0.24016 | 80 | 0.27447 | 80 | 0.30878 | 80 | 0.34308
85 | 0.017154 | 85 | 0.034308 | 85 | 0.068617 | 85 | 0.10293 | 85 | 0.13723 | 85 | 0.17154 | 85 | 0.20585 | 85 | 0.24016 | 85 | 0.27447 | 85 | 0.30878 | 85 | 0.34308
90 | 0.017154 | 90 | 0.034308 | 90 | 0.068617 | 90 | 0.10293 | 90 | 0.13723 | 90 | 0.17154 | 90 | 0.20585 | 90 | 0.24016 | 90 | 0.27447 | 90 | 0.30878 | 90 | 0.34308
95 | 0.017154 | 95 | 0.034308 | 95 | 0.068617 | 95 | 0.10293 | 95 | 0.13723 | 95 | 0.17154 | 95 | 0.20585 | 95 | 0.24016 | 95 | 0.27447 | 95 | 0.30878 | 95 | 0.34308
100 | 0.017154 | 100 | 0.034308 | 100 | 0.068617 | 100 | 0.10293 | 100 | 0.13723 | 100 | 0.17154 | 100 | 0.20585 | 100 | 0.24016 | 100 | 0.27447 | 100 | 0.30878 | 100 | 0.34308